Caledonian

Flame Retardant Databus Cables

www.caledonian-cables.co.uk	www.addison-cables.com

Flame Retardant RS485 Databus Cables

APPLICATION

The cables are designed for RS485 data connections where continued functionality is required during a fire situation. This cable combines low capacitance insulation with one of the highest levels of screening to provide high speed, interference free, data transmission where continued functionality is required during a fire situation.

STANDARDS

Basic design adapted to EIA/TIA 485

FIRE PERFORMANCE

Flame Retardance (Single Vertical EN 60332-1-2; IEC 60332-1-2; BS EN 60332-1-2; VDE Wire Test)** 0482-332-1 ; NBN C 30-004 (cat. F1); NF C32-070-2.1(C2);

CEI 20-35/1-2; EN 50265-2-1*; DIN VDE 0482-265-2-1*

| Reduced Fire Propagation | EN 60332-3-24 (cat. C); IEC 60332-3-24; BS EN 60332-3-24; |
| --- | --- |
| (Vertically-mounted bundled wires VDE 0482-332-3; NBN C 30-004 (cat. F2); NF C32-070-2.2(C1); |  |
| & cable test)** | CEI 20-22/3-4; EN 50266-2-4*; DIN VDE 0482-266-2-4 |

Note: Asterisk ** denotes that the standard compliance is optional, depending on the oxygen index of the PVC compound and the cable design.

CABLE CONSTRUCTION

Multipair RS 485 Overall Screened Databus Cable

Conductors: tinned copper wire, stranded according to IEC(EN) 60228 class 2. Insulation: Foam PE or foam skin PE.

Cabling Elements: Insulated cores are twisted to form pairs with varying lay length to minimize crosstalk. Two pair cable had four cores laid in quad formation.

Cabling: Pairs are cabled together in concentric layers.

Overall screen: Aluminum/polyester tape with tinned copper drain wire.

Outer Sheath: Thermoplastic PVC compound. UV resistance, hydrocarbon resistance, oil resistance, anti rodent and anti termite properties can be offered as option. Compliance to fire performance standard (IEC 60332-1, IEC 60332-3, UL 1581, UL 1666 etc) depends on the oxygen index of the PVC compound and the overall cable design. LSPVC can also be provided upon request.

ADDISON   111

ADDISON

Multipair RS 485 Overall Double Screened Databus Cable

Conductors: tinned copper wire, stranded according to IEC(EN) 60228 class 2. Insulation: Foam PE or foam skin PE.

Cabling Elements: Insulated cores are twisted to form pairs with varying lay length to minimize crosstalk. Two pair cable had four cores laid in quad formation.

Cabling: Pairs are cabled together in concentric layers. Overall screen: Aluminium/polyester tape+copper wire braid.

Outer Sheath: Thermoplastic PVC compound. UV resistance, hydrocarbon resistance, oil resistance, anti rodent and anti termite properties can be offered as option. Compliance to fire performance standard (IEC 60332-1, IEC 60332-3, UL 1581, UL 1666 etc) depends on the oxygen index of the PVC compound and the overall cable design. LSPVC can also be provided upon request.

Multipair RS 485 Individual & Overall screened Databus Cable Conductors: tinned copper wire, stranded according to IEC(EN) 60228 class 2. Insulation: Foam PE or foam skin PE.

Cabling Elements: Insulated cores are twisted to form pairs with varying lay length to minimize crosstalk. Two pair cable had four cores laid in quad formation.

Cabling: Pairs are cabled together in concentric layers. Individual Screen: Individual aluminium/polyester tape. Overall Screen: Copper wire braid.

Outer Sheath: Thermoplastic PVC compound. UV resistance, hydrocarbon resistance, oil resistance, anti rodent and anti termite properties can be offered as option. Compliance to fire performance standard (IEC 60332-1, IEC 60332-3, UL 1581, UL 1666 etc) depends on the oxygen index of the PVC compound and the overall cable design. LSPVC can also be provided upon request.

Multipair RS 485 Overall Screened Databus Cable

Conductors: tinned copper wire, stranded according to IEC(EN) 60228 class 2. Insulation: Foam PE or foam skin PE.

Cabling Elements: Insulated cores are twisted to form pairs with varying lay length to minimize crosstalk. Two pair cable had four cores laid in quad formation.

Cabling: Pairs are cabled together in concentric layers. Overall Screen: Copper wire braid.

Outer Sheath: Thermoplastic PVC compound. UV resistance, hydrocarbon resistance, oil resistance, anti rodent and anti termite properties can be offered as option. Compliance to fire performance standard (IEC 60332-1, IEC 60332-3, UL 1581, UL 1666 etc) depends on the oxygen index of the PVC compound and the overall cable design. LSPVC can also be provided upon request.

Physical AND THERMAL PROPERTIES

Temperature range during operation (fixed state):-20°C - +90°C

Temperature range during installation (mobile state): -5°C - +60°C Minimum bending radius: 8 x Overall Diameter

Electrical Properties

| Dielectric test | 1000 | V r.m.s. for 5’ (core-core) |
| --- | --- | --- |
|  | 1000 | V r.m.s. for 5’ (core-screen) |
| Impedance | 120Ω |  |
| Capacitance | 45 nF/km conductor to conductor |  |

112	Caledonian

Caledonian

Flame Retardant Databus Cables

www.caledonian-cables.co.uk	www.addison-cables.com

90 nF/km conductor to shield

CONSTRUCTION PARAMETERS

Multipair RS 485 Overall Screened Databus Cable

RE-02Y(St)Y / RE-02YS(St)Y

|  | Nominal |  |  | No./Nominal |  |  | Nominal |  |  | Nominal |  |  | Nominal |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| No.of | Cross |  |  |  |  |  |  |  |  |  |  |  |  | Approx. |  |  |  |
|  |  |  |  | Diameter of |  |  | Insulation |  |  | Sheath |  |  | Overall |  |  |  |  |
| pair x | Sectional |  |  |  |  |  |  |  |  |  |  |  |  | Weight |  |  |  |
|  |  |  |  | Strands |  |  | Thickness |  |  | Thickness |  |  | Diameter |  |  |  |  |
|  | Area |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | mm2 |  |  | No/mm |  |  | mm |  |  | mm |  |  | mm | kg/km |  |  |  |
| 1 | 0.22 |  |  | 7/0.2 |  |  | 0.55 |  |  | 0.40 |  |  | 4.0 | 21 |  |  |  |
| 2 | 0.22 |  |  | 7/0.2 |  |  | 0.55 |  |  | 0.40 |  |  | 7.1 | 42 |  |  |  |
| 4 | 0.22 |  |  | 7/0.2 |  |  | 0.55 |  |  | 0.40 |  |  | 8.3 | 68 |  |  |  |
| 1 | 0.50 |  |  | 16/0.2 |  |  | 0.55 |  |  | 0.40 |  |  | 4.6 | 32 |  |  |  |
| 2 | 0.50 |  |  | 16/0.2 |  |  | 0.55 |  |  | 0.40 |  |  | 8.2 | 68 |  |  |  |
| 4 | 0.50 |  |  | 16/0.2 |  |  | 0.55 |  |  | 0.40 |  |  | 9.8 | 115 |  |  |  |
| 1 | 0.75 |  |  | 24/0.2 |  |  | 0.55 |  |  | 0.40 |  |  | 5.1 | 40 |  |  |  |
| 2 | 0.75 |  |  | 24/0.2 |  |  | 0.55 |  |  | 0.40 |  |  | 9.1 | 84 |  |  |  |
| 4 | 0.75 |  |  | 24/0.2 |  |  | 0.55 |  |  | 0.40 |  |  | 10.9 | 144 |  |  |  |
| 1 | 1.00 |  |  | 30/0.2 |  |  | 0.55 |  |  | 0.40 |  |  | 5.2 | 49 |  |  |  |
| 2 | 1.00 |  |  | 30/0.2 |  |  | 0.55 |  |  | 0.40 |  |  | 9.5 | 105 |  |  |  |
| 4 | 1.00 |  |  | 30/0.2 |  |  | 0.55 |  |  | 0.40 |  |  | 11.2 | 182 |  |  |  |
| Multipair RS 485 Overall Double Screened Databus Cable |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| RE-02Y(St)CY / RE-02YS(St)CY |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Nominal |  |  | No./Nominal |  |  | Nominal |  |  | Nominal |  | Nominal |  |  |  |  |
| No.of |  | Cross |  |  |  |  |  |  |  |  |  |  |  |  | Approx. |  |  |
|  |  |  |  |  | Diameter of |  |  | Insulation |  |  | Sheath |  | Overall |  |  |  |  |
| pair x |  | Sectional |  |  |  |  |  |  |  |  |  |  |  |  | Weight |  |  |
|  |  |  |  |  | Strands |  |  | Thickness |  |  | Thickness |  | Diameter |  |  |  |  |
|  |  | Area |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | mm2 |  |  | No/mm |  |  | mm |  |  | mm |  | mm |  | kg/km |  |  |
| 1 |  | 0.22 |  |  | 7/0.2 |  |  | 0.55 |  |  | 0.40 |  | 4.5 |  | 34 |  |  |
| 2 |  | 0.22 |  |  | 7/0.2 |  |  | 0.55 |  |  | 0.40 |  | 7.5 |  | 67 |  |  |
| 4 |  | 0.22 |  |  | 7/0.2 |  |  | 0.55 |  |  | 0.40 |  | 8.8 |  | 97 |  |  |
| 1 |  | 0.50 |  |  | 16/0.2 |  |  | 0.55 |  |  | 0.40 |  | 5.1 |  | 48 |  |  |
| 2 |  | 0.50 |  |  | 16/0.2 |  |  | 0.55 |  |  | 0.40 |  | 8.7 |  | 97 |  |  |
| 4 |  | 0.50 |  |  | 16/0.2 |  |  | 0.55 |  |  | 0.40 |  | 10.3 |  | 150 |  |  |
| 1 |  | 0.75 |  |  | 24/0.2 |  |  | 0.55 |  |  | 0.40 |  | 5.6 |  | 57 |  |  |
| 2 |  | 0.75 |  |  | 24/0.2 |  |  | 0.55 |  |  | 0.40 |  | 9.7 |  | 116 |  |  |
| 4 |  | 0.75 |  |  | 24/0.2 |  |  | 0.55 |  |  | 0.40 |  | 11.4 |  | 182 |  |  |
| 1 |  | 1.00 |  |  | 30/0.2 |  |  | 0.55 |  |  | 0.40 |  | 5.7 |  | 67 |  |  |
| 2 |  | 1.00 |  |  | 30/0.2 |  |  | 0.55 |  |  | 0.40 |  | 10.0 |  | 138 |  |  |

ADDISON   113

ADDISON

| 4 |  | 1.00 | 30/0.2 |  |  |  | 0.55 |  |  | 0.40 | 11.8 |  | 222 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Multipair RS 485 Individual & Overall screened Databus Cable |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| RE-02Y(St)Y pimf / RE-02YS(St)Y pimf |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Nominal |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | No./Nominal |  | Nominal |  |  |  |  | Nominal | Nominal |  |  |  |  |
| No.of pair |  | Cross |  |  |  |  |  |  |  |  |  |  |  | Approx. |  |
|  |  |  | Diameter of |  | Insulation |  |  |  |  | Sheath | Overall |  |  |  |  |
| x |  | Sectional |  |  |  |  |  |  |  |  |  |  |  | Weight |  |
|  |  |  | Strands |  | Thickness |  |  |  |  | Thickness | Diameter |  |  |  |  |
|  |  | Area |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | mm2 | No/mm |  | mm |  |  |  |  | mm | mm |  |  | kg/km |  |
| 1 |  | 0.22 | 7/0.2 |  | 0.55 |  |  |  |  | 0.40 | 4.4 |  |  | 35 |  |
| 2 |  | 0.22 | 7/0.2 |  | 0.55 |  |  |  |  | 0.40 | 7.5 |  |  | 69 |  |
| 4 |  | 0.22 | 7/0.2 |  | 0.55 |  |  |  |  | 0.40 | 8.8 |  |  | 106 |  |
| 1 |  | 0.50 | 16/0.2 |  | 0.55 |  |  |  |  | 0.40 | 5.0 |  |  | 49 |  |
| 2 |  | 0.50 | 16/0.2 |  | 0.55 |  |  |  |  | 0.40 | 8.7 |  |  | 100 |  |
| 4 |  | 0.50 | 16/0.2 |  | 0.55 |  |  |  |  | 0.40 | 10.3 |  |  | 159 |  |
| 1 |  | 0.75 | 24/0.2 |  | 0.55 |  |  |  |  | 0.40 | 5.5 |  |  | 58 |  |
| 2 |  | 0.75 | 24/0.2 |  | 0.55 |  |  |  |  | 0.40 | 9.7 |  |  | 119 |  |
| 4 |  | 0.75 | 24/0.2 |  | 0.55 |  |  |  |  | 0.40 | 11.2 |  |  | 174 |  |
| 1 |  | 1.00 | 30/0.2 |  | 0.55 |  |  |  |  | 0.40 | 5.6 |  |  | 68 |  |
| 2 |  | 1.00 | 30/0.2 |  | 0.55 |  |  |  |  | 0.40 | 10.0 |  |  | 142 |  |
| 4 |  | 1.00 | 30/0.2 |  | 0.55 |  |  |  |  | 0.40 | 11.8 |  |  | 234 |  |
| Multipair RS 485 Overall Screened Databus Cable |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| RE-02YCY / RE-02YSCY |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Nominal |  | No./Nominal |  | Nominal |  |  |  | Nominal |  | Nominal |  |  |  |
| No.of pair |  | Cross |  |  |  |  |  |  |  |  |  |  |  | Approx. |  |
|  |  |  |  | Diameter of |  | Insulation |  |  |  | Sheath |  | Overall |  |  |  |
| x |  | Sectional |  |  |  |  |  |  |  |  |  |  |  | Weight |  |
|  |  |  |  | Strands |  | Thickness |  |  |  | Thickness |  | Diameter |  |  |  |
|  |  | Area |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | mm2 |  | No/mm |  | mm |  |  |  | mm |  | mm |  | kg/km |  |
| 1 |  | 0.22 |  | 7/0.2 |  | 0.55 |  |  |  | 0.40 |  | 4.3 |  | 31 |  |
| 2 |  | 0.22 |  | 7/0.2 |  | 0.55 |  |  |  | 0.40 |  | 7.3 |  | 61 |  |
| 4 |  | 0.22 |  | 7/0.2 |  | 0.55 |  |  |  | 0.40 |  | 8.5 |  | 91 |  |
| 1 |  | 0.50 |  | 16/0.2 |  | 0.55 |  |  |  | 0.40 |  | 4.9 |  | 44 |  |
| 2 |  | 0.50 |  | 16/0.2 |  | 0.55 |  |  |  | 0.40 |  | 8.5 |  | 91 |  |
| 4 |  | 0.50 |  | 16/0.2 |  | 0.55 |  |  |  | 0.40 |  | 10.0 |  | 142 |  |
| 1 |  | 0.75 |  | 24/0.2 |  | 0.55 |  |  |  | 0.40 |  | 5.4 |  | 53 |  |
| 2 |  | 0.75 |  | 24/0.2 |  | 0.55 |  |  |  | 0.40 |  | 9.5 |  | 109 |  |
| 4 |  | 0.75 |  | 24/0.2 |  | 0.55 |  |  |  | 0.40 |  | 11.2 |  | 174 |  |
| 1 |  | 1.00 |  | 30/0.2 |  | 0.55 |  |  |  | 0.40 |  | 5.5 |  | 63 |  |
| 2 |  | 1.00 |  | 30/0.2 |  | 0.55 |  |  |  | 0.40 |  | 9.8 |  | 131 |  |

114	Caledonian

Caledonian

Flame Retardant Databus Cables

www.caledonian-cables.co.uk	www.addison-cables.com

| 4 | 1.00 | 30/0.2 | 0.55 | 0.40 | 11.5 | 213 |
| --- | --- | --- | --- | --- | --- | --- |

TYPE CODES

RE-A-B-D

Outer Sheath

Y: PVC

Screen

St: Aluminum tape C: Copper braid

Insulation 02Y: Foam PE

02YS: Foam Skin PE

| 450/750V | NEIA/TIA485 | Flame Retardancy** | Reduced Fire Propagation** |
| --- | --- | --- | --- |
| Rated Voltage | Standard | NF C32-070-2.1(C2) | NF C32-070-2.2(C1) |
|  |  | IEC60332-1-2/EN50265-2-1 | IEC60332-3-24/EN50266-2-4 |

ADDISON   115