Caledonian

Flame Retardant Power & Control Cables

www.caledonian-cables.co.uk	www.addison-cables.com

600/1000V XLPE Insulated, PVC Sheathed, Armoured Power Cables (2-5 Cores)

FGD400 1RV-R (CU/XLPE/PVC 600/1000V Class 2)

FGD400 1RVMV-R (CU/XLPE/PVC/SWA/PVC 600/1000V Class 2)

APPLICATION

The cables are mainly used in power stations, mass transit underground passenger systems, airports, petrochemical plants, hotels, hospitals, and high-rise buildings.

STANDARDS

Basic design adapted to IEC 60502-1; BS 5467

FIRE PERFORMANCE

Flame Retardance (Single Vertical EN 60332-1-2; IEC 60332-1-2; BS EN 60332-1-2; VDE Wire Test)** 0482-332-1 ; NBN C 30-004 (cat. F1); NF C32-070-2.1(C2);

CEI 20-35/1-2; EN 50265-2-1*; DIN VDE 0482-265-2-1*

| Reduced Fire Propagation | EN 60332-3-24 (cat. C); IEC 60332-3-24; BS EN 60332-3-24; |
| --- | --- |
| (Vertically-mounted bundled wires VDE 0482-332-3; NBN C 30-004 (cat. F2); NF C32-070-2.2(C1); |  |
| & cable test)** | CEI 20-22/3-4; EN 50266-2-4*; DIN VDE 0482-266-2-4 |

Note: Asterisk ** denotes that the standard compliance is optional, depending on the oxygen index of the PVC compound and the cable design.

VOLTAGE RATING

600/1000V

CABLE CONSTRUCTION

Conductor: Plain annealed copper wire, stranded according to IEC(EN) 60228 class 2. Insulation: Extruded cross-linked XLPE compound.

Inner Sheath(optional): PVC Compound Armouring(optional): Galvanized Steel Wire

Outer Sheath: Thermoplastic PVC compound. UV resistance, hydrocarbon resistance, oil resistance, anti rodent and anti termite properties can be offered as option. Compliance to fire performance

ADDISON	47

ADDISON

standard (IEC 60332-1, IEC 60332-3, UL 1581, UL 1666 etc) depends on the oxygen index of the PVC compound and the overall cable design. LSPVC can also be provided upon request.

COLOUR CODE

Insulation Colour as per BS7671

|  | With Earth Conductor | Without Earth Conductor |
| --- | --- | --- |
| 2Cores | - | Brown, Blue |
| 3Cores | Yellow/Green, Brown, Blue | Brown, Gray, Black |
| 4Cores | Yellow/Green, Brown, Gray, Black | Brown, Gray, Black, Blue |
| 5Cores | Yellow/Green, Brown, Gray, Black, Blue | Brown, Gray, Black, Blue, Black |
| Above 5 Cores | Yellow/Green, Black Numbered | Black Numbered |

Sheath Colour: Black (other colors upon request)

Physical AND THERMAL PROPERTIES

Temperature range during operation: Max.90°C for XLPE

250°C in short-circuit for 5secs max. Minimum bending radius: 8 x Overall Diameter (unarmoured cable)

10 x Overall Diameter (armoured cable)

CONSTRUCTION PARAMETERS

|  | Conductor |  |  | FGD400 1RV-R |  |  |  | FGD400 1RVMV-R |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| No. of Core |  | No./ | Nominal | Unarmoured |  |  |  | Armoured |  |  |  |
| X |  | Nominal |  | Nominal |  |  | Diameter | Armour | Nominal |  |  |
|  |  |  | Insulation |  |  | Approx. |  |  |  | Approx. |  |
| Cross |  | Diameter of |  | Overall |  |  | Under | Wire | Overall |  |  |
| Section |  | Strands | Thickness | Diameter |  | Weight | Armour | Diameter | Diameter | Weight |  |
| mm2 |  | No./mm | mm | mm |  | mm | mm | mm | mm | kg/km |  |
|  |  |  |  |  | 2Cores |  |  |  |  |  |  |
| 2G1.5 |  | 7/0.53 | 0.7 | 10.0 |  | 126 | 8.5 | 0.9 | 13.9 | 350 |  |
| 2G2.5 |  | 7/0.67 | 0.7 | 10.8 |  | 158 | 9.3 | 0.9 | 14.7 | 400 |  |
| 2G4 |  | 7/0.85 | 0.7 | 11.9 |  | 205 | 10.4 | 0.9 | 15.8 | 475 |  |
| 2G6 |  | 7/1.04 | 0.7 | 13.0 |  | 264 | 11.5 | 0.9 | 16.9 | 560 |  |
| 2G10 |  | 7/1.35 | 0.7 | 14.9 |  | 378 | 13.4 | 1.25 | 19.5 | 810 |  |
| 2G16 |  | 7/1.70 | 0.7 | 17.0 |  | 534 | 15.5 | 1.25 | 21.6 | 980 |  |
| 2G25 |  | 7/2.14 | 0.9 | 20.4 |  | 650 | 18.9 | 1.6 | 25.7 | 1410 |  |
| 2G35 |  | 7/2.52 | 0.9 | 22.7 |  | 880 | 21.2 | 1.6 | 28.0 | 1930 |  |
|  |  |  |  |  | 3Cores |  |  |  |  |  |  |
| 3G1.5 |  | 7/0.53 | 0.7 | 10.5 |  | 145 | 9.0 | 0.9 | 14.4 | 390 |  |
| 3G2.5 |  | 7/0.67 | 0.7 | 11.4 |  | 185 | 9.9 | 0.9 | 15.3 | 450 |  |
| 3G4 |  | 7/0.85 | 0.7 | 12.5 |  | 247 | 11.0 | 0.9 | 16.4 | 540 |  |
| 3G6 |  | 7/1.04 | 0.7 | 13.8 |  | 323 | 11.6 | 1.25 | 17.7 | 745 |  |
| 3G10 |  | 7/1.35 | 0.7 | 15.8 |  | 474 | 14.3 | 1.25 | 20.4 | 950 |  |
| 3G16 |  | 7/1.70 | 0.7 | 18.0 |  | 682 | 16.5 | 1.25 | 23.0 | 1250 |  |

48	Caledonian

Caledonian

Flame Retardant Power & Control Cables

www.caledonian-cables.co.uk	www.addison-cables.com

| 3G25 | 7/2.14 | 0.9 | 21.7 | 910 | 20.2 | 1.6 | 27.0 | 1840 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 3G35 | 7/2.52 | 0.9 | 24.0 | 1180 | 22.4 | 1.6 | 29.2 | 2050 |
| 3G50 | 19/1.78 | 1.0 | 25.5 | 1600 | 24.2 | 1.6 | 31.2 | 2590 |
| 3G70 | 19/2.14 | 1.1 | 29.0 | 2240 | 28.2 | 2.0 | 36.2 | 3560 |
| 3G95 | 19/2.52 | 1.1 | 33.5 | 3050 | 31.7 | 2.0 | 40.1 | 4590 |
| 3G120 | 37/2.03 | 1.2 | 37.5 | 3800 | 36.0 | 2.0 | 44.6 | 5810 |
| 3G150 | 37/2.25 | 1.4 | 40.5 | 4640 | 39.5 | 2.5 | 49.5 | 6920 |
| 3G185 | 37/2.52 | 1.6 | 45.0 | 5870 | 43.3 | 2.5 | 53.5 | 8340 |
| 3G240 | 61/2.25 | 1.7 | 50.5 | 7670 | 48.4 | 2.5 | 59.0 | 10450 |
| 3G300 | 61/2.52 | 1.8 | 57.0 | 9460 | 54.4 | 2.5 | 65.4 | 12700 |
| 3G400 | 61/2.85 | 2.0 | 63.0 | 11945 | 57.8 | 2.5 | 70.0 | 15326 |
|  |  | 3Cores+1Core Earth Conductor |  |  |  |  |  |  |
| 3G10+6 | 7/1.35 | 0.7 | 16.5 | 543 | 17.6 | 1.25 | 20.1 | 1042 |
| 3G16+10 | 7/1.70 | 0.7 | 18.85 | 793 | 20.6 | 1.25 | 22.5 | 1567 |
| 3G25+10 | 7/2.14 | 0.9 | 22.1 | 1021 | 26.3 | 1.25 | 23.6 | 2091 |
| 3G25+16 | 7/2.14 | 0.9 | 23.0 | 1070 | 26.6 | 1.25 | 25.8 | 2150 |
| 3G35+16 | 19/1.53 | 0.9 | 24.3 | 1349 | 26.8 | 1.6 | 27.7 | 2390 |
| 3G35+25 | 19/1.53 | 0.9 | 25.2 | 1470 | 27.2 | 1.6 | 28.6 | 2505 |
| 3G50+16 | 19/1.78 | 1 | 26.1 | 1769 | 28.5 | 1.6 | 29.8 | 2916 |
| 3G50+25 | 19/1.78 | 1 | 27.3 | 1890 | 29.2 | 1.6 | 31.3 | 3107 |
| 3G50+35 | 19/1.78 | 1 | 27.8 | 1995 | 30.0 | 1.6 | 32.0 | 3175 |
| 3G70+25 | 19/2.14 | 1.1 | 30.2 | 2530 | 34.0 | 2.0 | 35.0 | 3203 |
| 3G70+35 | 19/2.14 | 1.1 | 30.9 | 2660 | 34.5 | 2.0 | 35.9 | 4067 |
| 3G70+50 | 19/2.14 | 1.1 | 31.5 | 2840 | 35 | 2.0 | 36.8 | 4310 |
| 3G95+16 | 19/2.52 | 1.1 | 34.6 | 3240 | 36.3 | 2.0 | 38.0 | 4856 |
| 3G95+25 | 19/2.52 | 1.1 | 35.1 | 3340 | 36.7 | 2.0 | 39.3 | 5047 |
| 3G95+35 | 19/2.52 | 1.1 | 36.0 | 3470 | 37.2 | 2.0 | 40.2 | 5115 |
| 3G95+50 | 19/2.52 | 1.1 | 36.8 | 3650 | 37.6 | 2.0 | 41.4 | 5289 |
| 3G120+35 | 37/2.03 | 1.2 | 38.2 | 3920 | 39.4 | 2.5 | 44.0 | 6160 |
| 3G120+50 | 37/2.03 | 1.2 | 39.1 | 4400 | 39.9 | 2.5 | 44.9 | 6473 |
| 3G120+70 | 37/2.03 | 1.2 | 40.0 | 4610 | 40.3 | 2.5 | 45.6 | 6793 |
| 3G120+95 | 37/2.03 | 1.2 | 41.2 | 4820 | 41.2 | 2.5 | 46.8 | 7120 |
| 3G150+50 | 37/2.25 | 1.4 | 41.5 | 5240 | 45.0 | 2.5 | 49.7 | 7549 |
| 3G150+50 | 37/2.25 | 1.4 | 42.3 | 5450 | 45.2 | 2.5 | 49.8 | 7565 |
| 3G150+95 | 37/2.25 | 1.4 | 43.6 | 5660 | 45.5 | 2.5 | 50.8 | 8196 |
| 3G150+120 | 37/2.25 | 1.4 | 44.8 | 6240 | 46.0 | 2.5 | 51.8 | 8590 |
| 3G185+70 | 37/2.52 | 1.6 | 46.0 | 6470 | 50.4 | 2.5 | 54.0 | 8950 |
| 3G185+95 | 37/2.52 | 1.6 | 47.5 | 6680 | 50.6 | 2.5 | 54.7 | 9573 |
| 3G185+120 | 37/2.52 | 1.6 | 47.9 | 6990 | 51.0 | 2.5 | 55.8 | 9968 |

ADDISON	49

ADDISON

| 3G185+150 | 37/2.52 | 1.6 | 48.5 | 7395 | 51.6 | 2.5 | 56.6 | 1023 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 3G240+70 | 61/2.25 | 1.7 | 49.2 | 7580 | 57.0 | 2.5 | 56.0 | 11294 |
| 3G240+95 | 61/2.25 | 1.7 | 52.3 | 8480 | 58.0 | 2.5 | 57.9 | 11620 |
| 3G240+120 | 61/2.25 | 1.7 | 53.4 | 8690 | 59.0 | 2.5 | 61.0 | 12015 |
| 3G240+150 | 61/2.25 | 1.7 | 54.9 | 9095 | 60.0 | 2.5 | 62.2 | 12373 |
| 3G300+95 | 61/2.52 | 1.8 | 55.6 | 9380 | 63 | 2.5 | 64.7 | 13803 |
| 3G300+120 | 61/2.52 | 1.8 | 58.1 | 10480 | 64.2 | 2.5 | 65.9 | 14197 |
| 3G300+150 | 61/2.52 | 1.8 | 57.3 | 11170 | 65.7 | 2.5 | 66.8 | 14556 |
| 3G300+185 | 61/2.52 | 1.8 | 58.7 | 11480 | 66.4 | 2.5 | 68.1 | 15015 |
| 3G300+240 | 61/2.52 | 1.8 | 62.4 | 11290 | 67 | 2.5 | 69.4 | 15697 |
|  |  | 4Cores |  |  |  |  |  |  |
| 4G1.5 | 7/0.53 | 0.7 | 11.3 | 169 | 10.0 | 0.9 | 15.4 | 430 |
| 4G2.5 | 7/0.67 | 0.7 | 12.3 | 220 | 10.8 | 0.9 | 16.2 | 505 |
| 4G4 | 7/0.85 | 0.7 | 13.6 | 297 | 12.1 | 0.9 | 17.5 | 710 |
| 4G6 | 7/1.04 | 0.7 | 15.0 | 392 | 13.5 | 1.25 | 19.6 | 855 |
| 4G10 | 7/1.35 | 0.7 | 17.2 | 585 | 15.7 | 1.25 | 21.8 | 1120 |
| 4G16 | 7/1.70 | 0.7 | 19.7 | 851 | 18.2 | 1.6 | 25.0 | 1600 |
| 4G25 | 7/2.14 | 0.9 | 23.9 | 1200 | 22.4 | 1.6 | 29.2 | 2160 |
| 4G35(S) | 7/2.52 | 0.9 | 25.0 | 1600 | 24.4 | 1.6 | 31.4 | 2560 |
| 4G50(S) | 19/1.78 | 1.0 | 28.0 | 2200 | 28.0 | 1.6 | 35.2 | 3180 |
| 4G70(S) | 19/2.14 | 1.1 | 32.0 | 3050 | 32.2 | 2.0 | 40.6 | 4490 |
| 4G95(S) | 19/2.52 | 1.1 | 37.0 | 4070 | 36.0 | 2.0 | 44.6 | 5725 |
| 4G120(S) | 37/2.03 | 1.2 | 42.0 | 5915 | 38.0 | 2.5 | 50.0 | 7550 |
| 4G150(S) | 37/2.25 | 1.4 | 46.0 | 6350 | 42.8 | 2.5 | 53.0 | 8555 |
| 4G185(S) | 37/2.52 | 1.6 | 50.0 | 7890 | 48.4 | 2.5 | 59.0 | 10560 |
| 4G240(S) | 61/2.25 | 1.7 | 57.0 | 10400 | 55.0 | 2.5 | 66.0 | 13180 |
| 4G300(S) | 61/2.52 | 1.8 | 63.0 | 12810 | 59.6 | 2.5 | 71.0 | 16100 |
| 4G400(S) | 61/2.85 | 2.0 | 71.0 | 15869 | 66.1 | 3.15 | 79.4 | 20715 |
| 4G500(S) | 61/3.20 | 2.2 | 78.0 | 20300 | 74.6 | 3.15 | 88.5 | 25347 |
|  |  | 4Cores+1Core Earth Conductor |  |  |  |  |  |  |
| 4G10+6 | 7/1.35 | 0.7 | 19 | 654 | 17.6 | 1.25 | 26.1 | 1362 |
| 4G16+10 | 7/1.70 | 0.7 | 21.95 | 962 | 20.6 | 1.25 | 27.3 | 1473 |
| 4G25+10 | 7/2.14 | 0.7 | 26.65 | 1311 | 26.3 | 1.25 | 32.6 | 1680 |
| 4G25+16 | 7/2.14 | 0.7 | 27.3 | 1369 | 26.6 | 1.25 | 33.4 | 2012 |
| 4G35+16 | 19/1.53 | 0.9 | 27.6 | 1769 | 25.6 | 1.6 | 44.5 | 2940 |
| 4G35+25 | 19/1.53 | 0.9 | 28.4 | 1890 | 26.2 | 1.6 | 46.2 | 3050 |
| 4G50+16 | 19/1.78 | 1 | 29.4 | 2369 | 28.5 | 1.6 | 48.2 | 3560 |

50	Caledonian

Caledonian

Flame Retardant Power & Control Cables

www.caledonian-cables.co.uk	www.addison-cables.com

| 4G50+25 | 19/1.78 | 1 | 31.6 | 2490 | 29.2 | 1.6 | 49.9 | 3670 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 4G50+35 | 19/1.78 | 1 | 33.6 | 3249 | 30.0 | 1.6 | 42.5 | 3759 |
| 4G70+25 | 19/2.14 | 1.1 | 34.2 | 3340 | 34 | 2.0 | 55.1 | 4980 |
| 4G70+35 | 19/2.14 | 1.1 | 35.6 | 3470 | 34.5 | 2.0 | 44.9 | 5036 |
| 4G70+50 | 19/2.14 | 1.1 | 37.8 | 3650 | 35 | 2.0 | 45.9 | 5468 |
| 4G95+16 | 19/2.52 | 1.1 | 41.5 | 4239 | 36.3 | 2.0 | 47.3 | 6105 |
| 4G95+25 | 19/2.52 | 1.1 | 42.6 | 4360 | 36.7 | 2.0 | 49.0 | 6215 |
| 4G95+35 | 19/2.52 | 1.1 | 43.3 | 4510 | 37.2 | 2.0 | 50.1 | 6325 |
| 4G95+50 | 19/2.52 | 1.1 | 44.1 | 4670 | 37.6 | 2.0 | 51.7 | 6455 |
| 4G120+35 | 37/2.03 | 1.2 | 42.6 | 6335 | 39.4 | 2.5 | 54.2 | 7968 |
| 4G120+50 | 37/2.03 | 1.2 | 43.8 | 6515 | 39.9 | 2.5 | 56.9 | 8280 |
| 4G120+70 | 37/2.03 | 1.2 | 45.9 | 6725 | 40.3 | 2.5 | 57.9 | 8511 |
| 4G120+95 | 37/2.03 | 1.2 | 46.4 | 6920 | 41.2 | 2.5 | 61.2 | 8790 |
| 4G150+70 | 37/2.25 | 1.4 | 47.3 | 6950 | 45.2 | 2.5 | 56.5 | 8879 |
| 4G150+95 | 37/2.25 | 1.4 | 48.5 | 7160 | 45.5 | 2.5 | 57.6 | 10179 |
| 4G150+120 | 37/2.25 | 1.4 | 50.2 | 7370 | 46.0 | 2.5 | 58.7 | 10739 |
| 4G185+70 | 37/2.52 | 1.6 | 53.7 | 7965 | 50.4 | 2.5 | 62.0 | 11200 |
| 4G185+95 | 37/2.52 | 1.6 | 52.4 | 8490 | 50.6 | 2.5 | 63.2 | 1263 |
| 4G185+120 | 37/2.52 | 1.6 | 53.9 | 8700 | 51.0 | 2.5 | 64.2 | 13050 |
| 4G185+150 | 37/2.52 | 1.6 | 55.6 | 8910 | 51.6 | 2.5 | 65.4 | 13680 |
| 4G240+70 | 61/2.25 | 1.7 | 59.4 | 9260 | 57 | 2.5 | 66.9 | 14140 |
| 4G240+95 | 61/2.25 | 1.7 | 59.4 | 9600 | 58 | 2.5 | 68.7 | 14420 |
| 4G240+120 | 61/2.25 | 1.7 | 61.9 | 11210 | 59.0 | 2.5 | 72.8 | 14763 |
| 4G240+150 | 61/2.25 | 1.7 | 63.4 | 11420 | 60.0 | 2.5 | 73.1 | 15241 |
| 4G300+95 | 61/2.52 | 1.8 | 67.8 | 12010 | 63 | 2.5 | 74.6 | 17467 |
| 4G300+120 | 61/2.52 | 1.8 | 64.0 | 12110 | 64.2 | 2.5 | 75.1 | 18050 |
| 4G300+150 | 61/2.52 | 1.8 | 66.1 | 13830 | 65.7 | 2.5 | 76.4 | 18662 |
| 4G300+185 | 61/2.52 | 1.8 | 71.5 | 14520 | 67 | 2.5 | 77.3 | 19031 |
| 4G300+240 | 61/2.52 | 1.8 | 72.0 | 14830 | 67 | 2.5 | 78.6 | 19878 |
|  |  |  | 5Cores |  |  |  |  |  |
| 5G1.5 | 7/0.53 | 0.7 | 13.7 | 205 | 9.9 | 0.9 | 18.6 | 537 |
| 5G2.5 | 7/0.67 | 0.7 | 14.9 | 265 | 10.8 | 0.9 | 19.6 | 631 |
| 5G4 | 7/0.85 | 0.7 | 16.3 | 360 | 12.1 | 0.9 | 21.2 | 860 |
| 5G6 | 7/1.04 | 0.7 | 18.2 | 478 | 15.8 | 1.5 | 23.7 | 1036 |
| 5G10 | 7/1.35 | 0.7 | 20.8 | 720 | 24 | 2.8 | 26.0 | 1358 |
| 5G16 | 7/1.70 | 0.7 | 24.2 | 1050 | 27 | 2.8 | 30.0 | 1940 |
| 5G25 | 7/2.14 | 0.9 | 29.4 | 1485 | 34 | 2.8 | 35.4 | 2619 |
| 5G35 | 19/1.53 | 0.9 | 30.3 | 1940 | 24.4 | 1.6 | 38.1 | 3140 |

ADDISON	51

ADDISON

| 5G50 | 19/1.78 | 1 | 34 | 2667 | 28.0 | 1.6 | 42.6 | 3555 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 5G70 | 19/2.14 | 1.1 | 38.5 | 3698 | 32.2 | 2.0 | 49.2 | 5444 |
| 5G95 | 19/2.52 | 1.1 | 44.6 | 4934 | 36.0 | 2.0 | 54.1 | 6941 |
| 5G120 | 37/2.03 | 1.2 | 5.8 | 7171 | 38.0 | 2.5 | 60.6 | 9154 |
| 5G150 | 37/2.25 | 1.4 | 55.6 | 7699 | 42.8 | 2.5 | 64.3 | 10372 |
| 5G185 | 37/2.52 | 1.6 | 60.4 | 9566 | 48.4 | 2.5 | 71.5 | 12828 |
| 5G240 | 61/2.25 | 1.7 | 69.1 | 12610 | 55.0 | 2.5 | 80 | 15980 |
| 5G300 | 61/2.52 | 1.8 | 76.4 | 15532 | 59.6 | 2.5 | 86.1 | 19521 |
| 5G400 | 61/2.85 | 2 | 86.1 | 19241 | 66.1 | 3.15 | 96.3 | 25116 |

(S) - Sectoral Stranded Conductors

Electrical PROPERTIES

Conductor Operating Temperature : 90°C

Ambient Temperature : 30°C

FGD400 1RZ1-R

Current-Carrying Capacities (Amp)

|  | Reference Method |  | Reference |  |  |  | Reference |  | Reference Method 12(free |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Conductor |  |  | Method 3 |  |  |  |  |  |  | air) |  |  |
| cross- | 4 (enclosed |  | (enclosed in |  | Reference Method |  | Method 11 (on a |  |  |  |  |  |
|  | in conduit |  |  |  |  |  | perforated cable |  | Horizontal | Vertical |  |  |
| sectional | in thermally |  | conduit on |  | 1 (clipped direct) |  | tray, horizontal or |  | flat | flat | Trefoil |  |
| area | insulating wall etc) |  | a wall or in |  |  |  | vertical) |  | spaced | spaced |  |  |
|  |  |  | trunking etc) |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | 2 cables, | 2 |  |  |
|  |  |  |  |  |  |  |  |  |  | cables, |  |  |
|  | 2 |  | 2 |  | 2 cables, | 3 or 4 | 2 cables, | 3 or 4 | single- | single- |  |  |
|  |  |  |  | 3 or 4 | single- | cables, | single- | cables, | phase |  |  |  |
|  | cables, | 3 or 4 | cables, |  |  |  |  |  |  | phase | 3 cables, |  |
|  | single- | cables, | single- | cables, | phase | 3-phase | phase | 3-phase | a.c. or | a.c. or | trefoil |  |
|  | phase | 3-phase | phase | 3- | a.c. or | a.c. flat | a.c. or | a.c. flat | d.c. | d.c. | 3-phase |  |
|  |  |  |  | phase | d.c. flat | and | d.c. or | and | or 3 c |  |  |  |
|  | a.c. or | a.c. | a.c. or |  |  |  |  |  |  | or 3 | a.c. |  |
|  | d.c. |  | d.c | a.c. | and | touching | flat and | touching | ables | cables |  |  |
|  |  |  |  |  | touching | or trefoil | touching | or trefoil | three |  |  |  |
|  |  |  |  |  |  |  |  |  |  | three |  |  |
|  |  |  |  |  |  |  |  |  | phase |  |  |  |
|  |  |  |  |  |  |  |  |  |  | phase |  |  |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 |  |
| mm2 | A | A | A | A | A | A | A | A | A | A | A |  |
| 1.5 | 18 | 17 | 22 | 19 | 25 | 23 | - | - | - | - | - |  |
| 2.5 | 24 | 23 | 30 | 26 | 34 | 31 | - | - | - | - | - |  |
| 4 | 33 | 30 | 40 | 35 | 46 | 41 | - | - | - | - | - |  |
| 6 | 43 | 39 | 51 | 45 | 59 | 54 | - | - | - | - | - |  |
| 10 | 58 | 53 | 71 | 63 | 81 | 74 | - | - | - | - | - |  |
| 16 | 76 | 70 | 95 | 85 | 109 | 99 | - | - | - | - | - |  |
| 25 | 100 | 91 | 126 | 111 | 143 | 130 | 158 | 140 | 183 | 163 | 138 |  |
| 35 | 125 | 111 | 156 | 138 | 176 | 161 | 195 | 176 | 226 | 203 | 171 |  |
| 50 | 149 | 135 | 189 | 168 | 228 | 209 | 293 | 215 | 274 | 246 | 209 |  |

52	Caledonian

Caledonian

Flame Retardant Power & Control Cables

www.caledonian-cables.co.uk	www.addison-cables.com

| 70 | 189 | 170 | 240 | 214 | 293 | 268 | 308 | 279 | 351 | 318 | 270 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 95 | 228 | 205 | 290 | 259 | 355 | 326 | 375 | 341 | 426 | 389 | 330 |
| 120 | 263 | 235 | 336 | 299 | 413 | 379 | 436 | 398 | 495 | 453 | 385 |
| 150 | 300 | 270 | 375 | 328 | 476 | 436 | 505 | 461 | 570 | 524 | 445 |
| 185 | 341 | 306 | 426 | 370 | 545 | 500 | 579 | 530 | 651 | 600 | 511 |
| 240 | 400 | 358 | 500 | 433 | 644 | 590 | 686 | 630 | 769 | 711 | 606 |
| 300 | 459 | 410 | 573 | 493 | 743 | 681 | 794 | 730 | 886 | 824 | 701 |
| 400 | - | - | 684 | 584 | 868 | 793 | 915 | 849 | 1065 | 994 | 820 |
| 500 | - | - | 783 | 666 | 990 | 904 | 1044 | 973 | 1228 | 1150 | 936 |

Voltage Drop (Per Amp Per Meter)

|  |  | 2 cables, single-phase a.c. |  |  |  |  |  |  |  | 3 or 4 cables, 3-phase a.c. |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Size of | 2 | Ref. Methods 3 |  |  | Ref. Methods 1 |  |  | Ref. Methods 3 |  |  | Ref. Methods 1, |  |  |  |  | Ref. Methods 1 |  |  |  |
|  | cables | and 4 (enclosed |  |  | and 11 (clipped |  |  | and 4 (enclosed |  |  |  |  |  |  |  |  |  |  |  |
| conductor |  |  |  |  |  |  |  |  |  |  | 11 and 12 (in |  |  |  |  | and 11 |  |  |  |
|  | d.c. | in conduit etc, in |  |  | direct or on trays |  |  | in conduit etc, in |  |  |  | trefoil) |  |  |  | (Flat and touching) |  |  |  |
|  |  | or on a wall) |  |  | touching) |  |  | or on a wall) |  |  |  |  |  |  |  |  |  |  |  |
| 1 | 2 |  | 3 |  | 4 |  |  |  | 5 |  |  | 6 |  |  |  | 7 |  |  |  |
| mm2 | mV/A/m | mV/A/m |  |  | mV/A/m |  |  | mV/A/m |  |  |  | mV/A/m |  |  |  | mV/A/m |  |  |  |
| 1.5 | 31 |  | 31 |  | 27 |  |  |  | 27 |  |  | 27 |  |  |  | 27 |  |  |  |
| 2.5 | 19 |  | 19 |  | 16 |  |  |  | 16 |  |  | 16 |  |  |  | 16 |  |  |  |
| 4 | 33 |  | 12 |  | 10 |  |  |  | 10 |  |  | 10 |  |  |  | 10 |  |  |  |
| 6 | 7.8 |  | 7.9 |  | 6.8 |  |  |  | 6.8 |  |  | 6.8 |  |  |  | 6.8 |  |  |  |
| 10 | 4.7 |  | 4.7 |  | 4.7 |  |  |  | 4 |  |  | 4 |  |  |  | 4 |  |  |  |
| 16 | 2.9 |  | 2.9 |  | 2.9 |  |  |  | 2.5 |  |  | 2.5 |  |  |  | 2.5 |  |  |  |
|  |  | r | x | z | r | x | z | r | x | z | r |  | x |  | z | r | x | z |  |
| 25 | 1.85 | 1.85 | 0.31 | 1.90 | 1.85 | 0.190 | 1.85 | 1.60 | 0.27 | 1.65 | 1.600 |  | 0.165 | 1.600 |  | 1.600 | 0.190 | 1.600 |  |
| 35 | 1.35 | 1.35 | 0.29 | 1.35 | 1.35 | 0.180 | 1.35 | 1.15 | 0.25 | 1.15 | 1.150 |  | 0.155 |  | 1.50 | 1.150 | 0.180 | 1.150 |  |
| 50 | 0.99 | 1.00 | 0.29 | 1.05 | 0.99 | 0.180 | 1.00 | 0.87 | 0.25 | 0.90 | 0.860 |  | 0.155 | 0.870 |  | 0.860 | 0.180 | 0.870 |  |
| 70 | 0.68 | 0.70 | 0.28 | 0.75 | 0.68 | 0.175 | 0.71 | 0.60 | 0.24 | 0.65 | 0.590 |  | 0.150 | 0.610 |  | 0.590 | 0.175 | 0.620 |  |
| 95 | 0.49 | 0.51 | 0.27 | 0.58 | 0.49 | 0.170 | 0.52 | 0.44 | 0.23 | 0.50 | 0.430 |  | 0.145 | 0.450 |  | 0.430 | 0.170 | 0.460 |  |
| 120 | 0.39 | 0.41 | 0.26 | 0.48 | 0.39 | 0.165 | 0.43 | 0.35 | 0.23 | 0.42 | 0.340 |  | 0.140 | 0.370 |  | 0.340 | 0.165 | 0.380 |  |
| 150 | 0.32 | 0.33 | 0.26 | 0.43 | 0.32 | 0.165 | 0.36 | 0.29 | 0.23 | 0.37 | 0.280 |  | 0.140 | 0.310 |  | 0.280 | 0.165 | 0.320 |  |
| 185 | 0.25 | 0.27 | 0.26 | 0.37 | 0.26 | 0.165 | 0.30 | 0.23 | 0.23 | 0.32 | 0.220 |  | 0.140 | 0.260 |  | 0.220 | 0.165 | 0.280 |  |
| 240 | 0.19 | 0.21 | 0.26 | 0.33 | 0.20 | 0.160 | 0.25 | 0.185 | 0.22 | 0.29 | 0.170 |  | 0.140 | 0.220 |  | 0.170 | 0.165 | 0.240 |  |
| 300 | 0.155 | 0.175 | 0.25 | 0.31 | 0.16 | 0.160 | 0.22 | 0.150 | 0.22 | 0.27 | 0.140 |  | 0.140 | 0.195 |  | 0.135 | 0.160 | 0.210 |  |
| 400 | 0.12 | 0.140 | 0.25 | 0.29 | 0.13 | 0.155 | 0.20 | 0.125 | 0.22 | 0.25 | 0.110 |  | 0.135 | 0.175 |  | 0.110 | 0.160 | 0.195 |  |
| 500 | 0.093 | 0.120 | 0.25 | 0.28 | 0.105 | 0.155 | 0.185 | 0.100 | 0.22 | 0.24 | 0.090 |  | 0.135 | 0.160 |  | 0.088 | 0.160 | 0.180 |  |

ADDISON	53

ADDISON

FGD400 1RZ1MZ1-R

Current-Carrying Capacities (Amp)

|  | Reference |  | Reference Method 11 (on |  | In single-way |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | a perforated horizontal |  |  |  | Laid direct in ground |  |  |
|  | Method 1 (clipped |  |  |  |  |  |  |  |  |
|  |  |  | cable trayor Reference |  | ducts |  |  |  |  |
|  | direct) |  |  |  |  |  |  |  |  |
| Conductor |  |  | Method 13 [free air] ) |  |  |  |  |  |  |
| cross- | one | one |  |  | one | one | one | one |  |
| sectional | 2-core | 3-core |  | one 3-core | 2-core |  | 2-core |  |  |
|  |  |  | one 2-core |  |  | 3-core or |  | 3-core or |  |
| area | cable | or | cable single | or 4-core | cable | 4-core | cable | 4-core |  |
|  | single | 4-core |  | cable | single |  | single |  |  |
|  | phase | cable | phase a.c. | 3-phase | phase | cable | phase | cable |  |
|  |  |  | or d.c. |  |  | 3-phase |  | 3-phase |  |
|  | a.c. or | 3-phase |  | a.c. | a.c. or |  | a.c. or |  |  |
|  |  |  |  |  |  | a.c. |  | a.c. |  |
|  | d.c. | a.c. |  |  | d.c. |  | d.c. |  |  |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |  |
| mm2 | A | A | A | A | A | A | A | A |  |
| 1.5 | 27 | 23 | 29 | 25 | - | 23 | - | 28 |  |
| 2.5 | 36 | 31 | 39 | 33 | - | 30 | - | 36 |  |
| 4 | 49 | 42 | 52 | 44 | - | 40 | - | 48 |  |
| 6 | 62 | 53 | 66 | 56 | - | 50 | - | 60 |  |
| 10 | 85 | 73 | 90 | 78 | - | 65 | - | 80 |  |
| 16 | 110 | 94 | 115 | 99 | 115 | 94 | 140 | 115 |  |
| 25 | 146 | 124 | 152 | 131 | 145 | 125 | 180 | 150 |  |
| 35 | 180 | 154 | 188 | 162 | 175 | 150 | 215 | 180 |  |
| 50 | 219 | 187 | 228 | 197 | 210 | 175 | 255 | 215 |  |
| 70 | 279 | 238 | 291 | 251 | 260 | 215 | 315 | 265 |  |
| 95 | 338 | 289 | 354 | 304 | 310 | 260 | 380 | 315 |  |
| 120 | 392 | 335 | 410 | 353 | 355 | 300 | 430 | 360 |  |
| 150 | 451 | 386 | 472 | 406 | 400 | 335 | 480 | 405 |  |
| 185 | 515 | 441 | 539 | 463 | 455 | 380 | 540 | 460 |  |
| 240 | 607 | 520 | 636 | 546 | 520 | 440 | 630 | 530 |  |
| 300 | 698 | 599 | 732 | 628 | 590 | 495 | 700 | 590 |  |
| 400 | 787 | 673 | 847 | 728 | 660 | 560 | 790 | 670 |  |

Voltage Drop (Per Amp Per Meter)

|  |  |  |  |  | 2 cables, | 3 or 4 |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | single- | cables, |  |
|  | Conductor | 2-core | 2 cables, single-phase | 3 or 4 cables, 3-phase | phase | 3-phase |  |
|  | cross-sectional |  |  |  | a.c. | a.c. |  |
|  |  | cable d.c. | a.c. | a.c. |  |  |  |
|  | area |  |  |  | In ducts or | In ducts |  |
|  |  |  |  |  |  | or |  |
|  |  |  |  |  | in ground |  |  |
|  |  |  |  |  |  | in ground |  |
|  | 1 | 2 | 3 | 4 | 5 | 6 |  |
|  | mm2 | mV/A/m | mV/A/m | mV/A/m | mV/A/m | mV/A/m |  |
|  | 1.5 | 31.0 | 31.0 | 27.0 | 31.0 | 25.0 |  |
| 54 | Caledonian |  |  |  |  |  |  |

Caledonian

Flame Retardant Power & Control Cables

www.caledonian-cables.co.uk	www.addison-cables.com

| 2.5 |  |  | 19.0 |  |  | 19.0 |  |  | 16.0 |  |  | 19.0 |  |  | 15.0 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 4 |  |  | 12.0 |  |  | 12.0 |  |  | 10.0 |  |  | 12.0 |  |  | 9.7 |
| 6 |  |  | 7.9 |  |  | 7.9 |  |  | 6.8 |  |  | 7.9 |  |  | 6.5 |
| 10 |  |  | 4.7 |  |  | 4.7 |  |  | 4.0 |  |  | 4.7 |  |  | 3.9 |
| 16 |  |  | 2.9 |  |  | 2.9 |  |  | 2.5 |  |  | 2.9 |  |  | 2.6 |
|  |  |  |  | r |  | x | z | r | x |  | z |  |  |  |  |
| 25 |  |  | 1.850 | 1.350 |  | 0.160 | 1.900 | 1.600 | 0.140 |  | 1.650 | 1.900 |  |  | 1.600 |
| 35 |  |  | 1.350 | 1.350 |  | 0.155 | 1.350 | 1.150 | 0.135 |  | 1.150 | 1.350 |  |  | 1.200 |
| 50 |  |  | 0.980 | 0.990 |  | 0.155 | 1.000 | 0.860 | 0.135 |  | 0.870 | 1.000 |  |  | 0.870 |
| 70 |  |  | 0.670 | 0.670 |  | 0.150 | 0.690 | 0.590 | 0.130 |  | 0.600 | 0.690 |  |  | 0.610 |
| 95 |  |  | 0.490 | 0.500 |  | 0.150 | 0.520 | 0.430 | 0.130 |  | 0.450 | 0.520 |  |  | 0.450 |
| 120 |  |  | 0.390 | 0.400 |  | 0.145 | 0.420 | 0.340 | 0.130 |  | 0.370 | 0.420 |  |  | 0.360 |
| 150 |  |  | 0.310 | 0.320 |  | 0.145 | 0.350 | 0.280 | 0.125 |  | 0.300 | 0.350 |  |  | 0.300 |
| 185 |  |  | 0.250 | 0.260 |  | 0.145 | 0.290 | 0.220 | 0.125 |  | 0.260 | 0.290 |  |  | 0.250 |
| 240 |  |  | 0.195 | 0.200 |  | 0.140 | 0.240 | 0.175 | 0.125 |  | 0.210 | 0.240 |  |  | 0.210 |
| 300 |  |  | 0.155 | 0.160 |  | 0.140 | 0.210 | 0.140 | 0.120 |  | 0.185 | 0.210 |  |  | 0.190 |
| 400 |  |  | 0.120 | 0.130 |  | 0.140 | 0.190 | 0.115 | 0.120 |  | 0.165 | 0.190 |  |  | 0.180 |
|  | 600/1000V | IECN60502-1 |  |  | NBS5467 |  | Flame Retardancy** |  |  | Reduced Fire Propagation** |  |  |  |  |  |
|  | Rated Voltage |  |  |  | Standard |  | NF C32-070-2.1(C2) |  |  | NF C32-070-2.2(C1) |  |  |  |  |  |
|  |  | Standard |  |  |  |  | IEC60332-1-2/EN50265-2-1 |  |  | IEC60332-3-24/EN50266-2-4 |  |  |  |  |  |

ADDISON	55