Caledonian

Flame Retardant Power & Control Cables

www.caledonian-cables.co.uk	www.addison-cables.com

600/1000V XLPE Insulated, PVC Sheathed, Double steel tape Armoured Power Cables (3 Cores)

FGD400 1RVMV-R (CU/XLPE/PVC/DSTA/PVC 600/1000V Class 2)

APPLICATION

The cables are mainly used in power stations, mass transit underground passenger systems, airports, petrochemical plants, hotels, hospitals, and high-rise buildings.

STANDARDS

Basic design adapted to IEC 60502-1

FIRE PERFORMANCE

Flame Retardance (Single Vertical EN 60332-1-2; IEC 60332-1-2; BS EN 60332-1-2; VDE Wire Test)** 0482-332-1 ; NBN C 30-004 (cat. F1); NF C32-070-2.1(C2);

CEI 20-35/1-2; EN 50265-2-1*; DIN VDE 0482-265-2-1*

| Reduced Fire Propagation | EN 60332-3-24 (cat. C); IEC 60332-3-24; BS EN 60332-3-24; |
| --- | --- |
| (Vertically-mounted bundled wires VDE 0482-332-3; NBN C 30-004 (cat. F2); NF C32-070-2.2(C1); |  |
| & cable test)** | CEI 20-22/3-4; EN 50266-2-4*; DIN VDE 0482-266-2-4 |

Note: Asterisk ** denotes that the standard compliance is optional, depending on the oxygen index of the PVC compound and the cable design.

VOLTAGE RATING

600/1000V

CABLE CONSTRUCTION

Conductor: Plain annealed copper wire, normal stranded or compact stranded according to IEC(EN) 60228 class 2.

Insulation: Extruded cross-linked XLPE compound.

Filler, binder and inner covering: PP, PET, PVC

Armouring: Double steel tape

Outer Sheath: Thermoplastic PVC compound. UV resistance, hydrocarbon resistance, oil resistance,

ADDISON	73

ADDISON

anti rodent and anti termite properties can be offered as option. Compliance to fire performance standard (IEC 60332-1, IEC 60332-3, UL 1581, UL 1666 etc) depends on the oxygen index of the PVC compound and the overall cable design. LSPVC can also be provided upon request.

COLOUR CODE

Insulation Colour as per BS7671

|  | With Earth Conductor | Without Earth Conductor |
| --- | --- | --- |
| 2Cores | - | Brown, Blue |
| 3Cores | Yellow/Green, Brown, Blue | Brown, Gray, Black |
| 4Cores | Yellow/Green, Brown, Gray, Black | Brown, Gray, Black, Blue |
| 5Cores | Yellow/Green, Brown, Gray, Black, Blue | Brown, Gray, Black, Blue, Black |
| Above 5 Cores | Yellow/Green, Black Numbered | Black Numbered |

Sheath Colour: Black (other colors upon request)

Physical AND THERMAL PROPERTIES

Temperature range during operation: Max.90°C for XLPE

250°C in short-circuit for 5secs max.

Minimum bending radius: 10x Overall Diameter

CONSTRUCTION PARAMETERS

|  | Conductor |  |  |  |  |  | FGD400 1RVMV-R |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Nominal |  | InsulationNominal |  |  |  |  |  |  |
|  | Phases | Neutral | Diameter |  |  |  |  |  |  |  |  |
|  |  |  | Overall |  | Thickness |  | Nominal | Nominal | Nominal |  |  |
|  |  |  | Conducrtor |  |  |  |  |  |  |  |  |
| No. of Core X |  |  |  |  |  |  | Steel | Sheath | Overall | Approx. |  |
| Cross Section |  |  |  |  |  |  | Tape |  |  | Weight |  |
|  | No./ | No./ |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | Thickness | Diatemer |  |  |
|  | Nominal | Nominal |  |  |  |  | Thickness |  |  |  |  |
|  | Diameter | Diameter | Pha. | Neu. | Pha. | Neu. |  |  |  |  |  |
|  | of | of |  |  |  |  |  |  |  |  |  |
|  | Strands | Strands |  |  |  |  |  |  |  |  |  |
| mm2 | No/mm | No/mm | mm | mm | mm | mm | mm | mm | mm | Kg/km |  |
| 3x10+1x6 | 7/1.35 | 7/1.04 | 3.75 | 2.90 | 0.7 | 0.7 | 0.2 | 1.8 | 20.1 | 740 |  |
| 3x16+1x10 | 7/1.70 | 7/1.35 | 4.75 | 3.75 | 0.7 | 0.7 | 0.2 | 1.8 | 22.5 | 1,004 |  |
| 3x25+2x16 | 7/2.14 | 7/1.70 | 5.85 | 4.75 | 0.9 | 0.7 | 0.2 | 1.8 | 25.8 | 1,421 |  |
| 3x35+1x16 | 7/2.52 | 7/1.70 | 6.90 | 4.75 | 0.9 | 0.7 | 0.2 | 1.8 | 27.7 | 1,745 |  |
| 3x35+1x25 | 7/2.52 | 7/2.14 | 6.90 | 5.85 | 0.9 | 0.9 | 0.2 | 1.8 | 28.6 | 1,864 |  |
| 3x50+1x25 | 19/1.78 | 7/2.14 | 8.15 | 5.85 | 1.0 | 0.9 | 0.2 | 1.8 | 31.3 | 2,358 |  |
| 3x50+1x35 | 19/1.78 | 7/2.52 | 8.15 | 6.90 | 1.0 | 0.9 | 0.2 | 1.9 | 32.0 | 2.72 |  |
| 3x70+1x35 | 19/2.14 | 7/2.52 | 9.75 | 6.90 | I.1 | 0.9 | 0.2 | 2.0 | 35.9 | 3166 |  |
| 3x70+1x50 | 19/2.14 | 19/1.78 | 9.75 | 8.15 | I.1 | 1.0 | 0.2 | 2.0 | 36.8 | 3.341 |  |
| 3x95+1x50 | 19/2.52 | 19/1.78 | 11.4 | 8.15 | I.1 | 1.0 | 0.5 | 2.1 | 41.4 | 4,611 |  |

74	Caledonian

Caledonian

Flame Retardant Power & Control Cables

www.caledonian-cables.co.uk	www.addison-cables.com

| 3x120+1x70 | 37/2.03 | 19/2.14 | 12.8 | 9.75 | 1.2 | I.1 | 0.5 | 2.3 | 45.6 | 5682 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 3x150+1x95 | 37/2.25 | 19/2.52 | 14.3 | 11.4 | 1.4 | I.1 | 0.5 | 2.4 | 50.8 | 7,072 |
| 3x150+1x120 | 37/2.25 | 37/2.03 | 14.3 | 12.8 | 1.4 | 1.2 | 0.5 | 2.5 | 51.8 | 7,357 |
| 3x185+1x95 | 37/2.52 | 19/2.52 | 15.9 | 11.4 | 1.6 | I.1 | 0.5 | 2.6 | 54.7 | 8,348 |
| 3x185+1x120 | 37/2.52 | 37/2.03 | 15.9 | 12.8 | 1.6 | 1.2 | 0.5 | 2.6 | 55.8 | 8638 |
| 3x240+1x120 | 61/2.25 | 37/2.03 | 18.2 | 12.8 | 1.7 | 1.2 | 0.5 | 2.7 | 61.0 | 10,660 |
| 3x240+1x150 | 61/2.25 | 37/2.25 | 18.2 | 14.3 | 1.7 | 1.4 | 0.5 | 2.8 | 62.2 | 11024 |
| 3x300+1x150 | 61/2.52 | 37/2.25 | 20.4 | 14.3 | 1.8 | 1.4 | 0.5 | 2.9 | 66.8 | 12,809 |
| 3x300+1x185 | 61/2.52 | 37/2.52 | 20.4 | 15.9 | 1.8 | 1.6 | 0.5 | 3.0 | 68.1 | 13,256 |

Notes:

- *All conductors in accordance with lEC 60228. Compact shape (Com.) or non-compact depending on order.

- Beside above list we can also provide others size depend on customer’s requirement.

Electrical PROPERTIES

|  |  | Conductor |  |  |  | Max.DC resistance of |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Phases | Neutral |  | Dia.Overall |  |  |  |  |
|  |  |  |  |  |  | conductor @20°C |  |  |
| No. of Core X |  |  |  | Conducrtor |  |  |  |  |
| Cross Section | No./Nominal | No./Nominal |  |  |  |  |  |  |
|  | Diameter of | Diameter of |  | Pha. | Neu. | Pha. | Neu. |  |
|  | Strands | Strands |  |  |  |  |  |  |
| mm2 | No/mm | No/mm |  | mm | mm | Ω/km | Ω/km |  |
| 3x10+1x6 | 7/1.35 | 7/1.04 |  | 3.75 | 2.90 | 1.83 | 3.08 |  |
| 3x16+1x10 | 7/1.70 | 7/1.35 |  | 4.75 | 3.75 | 1.15 | 1.83 |  |
| 3x25+2x16 | 7/2.14 | 7/1.70 |  | 5.85 | 4.75 | 0.727 | 1.15 |  |
| 3x35+1x16 | 7/2.52 | 7/1.70 |  | 6.90 | 4.75 | 0.524 | 1.15 |  |
| 3x35+1x25 | 7/2.52 | 7/2.14 |  | 6.90 | 5.85 | 0.524 | 0.727 |  |
| 3x50+1x25 | 19/1.78 | 7/2.14 |  | 8.15 | 5.85 | 0.387 | 0.727 |  |
| 3x50+1x35 | 19/1.78 | 7/2.52 |  | 8.15 | 6.90 | 0.387 | 0.524 |  |
| 3x70+1x35 | 19/2.14 | 7/2.52 |  | 9.75 | 6.90 | 0268 | 0.524 |  |
| 3x70+1x50 | 19/2.14 | 19/1.78 |  | 9.75 | 8.15 | 0268 | 0.387 |  |
| 3x95+1x50 | 19/2.52 | 19/1.78 |  | 11.4 | 8.15 | 0.193 | 0.387 |  |
| 3x120+1x70 | 37/2.03 | 19/2.14 |  | 12.8 | 9.75 | 0.153 | 0.268 |  |
| 3x150+1x95 | 37/2.25 | 19/2.52 |  | 14.3 | 11.4 | 0.124 | 0.193 |  |
| 3x150+1x120 | 37/2.25 | 37/2.03 |  | 14.3 | 12.8 | 0.124 | 0.153 |  |
| 3x185+1x95 | 37/2.52 | 19/2.52 |  | 15.9 | 11.4 | 0.0991 | 0.193 |  |
| 3x185+1x120 | 37/2.52 | 37/2.03 |  | 15.9 | 12.8 | 0.0991 | 0.153 |  |
| 3x240+1x120 | 61/2.25 | 37/2.03 |  | 18.2 | 12.8 | 0.0754 | 0.153 |  |
| 3x240+1x150 | 61/2.25 | 37/2.25 |  | 18.2 | 14.3 | 0.0754 | 0.124 |  |
| 3x300+1x150 | 61/2.52 | 37/2.25 |  | 20.4 | 14.3 | 0.0601 | 0.124 |  |
| 3x300+1x185 | 61/2.52 | 37/2.52 |  | 20.4 | 15.9 | 0.0601 | 0.0991 |  |

ADDISON	75

ADDISON

Electrical PROPERTIES

Conductor Operating Temperature : 90°C

Ambient Temperature : 30°C

Current-Carrying Capacities (Amp)

|  |  |  | Reference Method |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Reference Method |  | 11 (on a perforated |  | In single-way |  | Laid direct in |  |  |
|  | 1 (clipped |  | horizontal cable trayor |  |  |  |  |  |  |
|  |  |  |  |  | ducts |  | ground |  |  |
| Conductor | direct) |  | Reference Method 13 |  |  |  |  |  |  |
|  |  |  | [free air] ) |  |  |  |  |  |  |
| cross- |  |  |  |  |  |  |  |  |  |
|  | one |  |  |  | one |  | one |  |  |
| sectional |  | one |  |  |  | one |  | one |  |
|  | 2-core |  |  | one 3-core | 2-core |  | 2-core |  |  |
| area |  | 3-core or | one 2-core |  |  | 3-core or |  | 3-core or |  |
|  | cable | 4-core | cable single | or 4-core | cable | 4-core | cable | 4-core |  |
|  | single |  |  | cable | single |  | single |  |  |
|  |  | cable | phase a.c. |  |  | cable |  | cable |  |
|  | phase |  |  | 3-phase | phase |  | phase |  |  |
|  |  | 3-phase | or d.c. |  |  | 3-phase |  | 3-phase |  |
|  | a.c. or | a.c. |  | a.c. | a.c. or | a.c. | a.c. or | a.c. |  |
|  | d.c. |  |  |  | d.c. |  | d.c. |  |  |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |  |
| mm2 | A | A | A | A | A | A | A | A |  |
| 10 | 85 | 73 | 90 | 78 | - | 65 | - | 80 |  |
| 16 | 110 | 94 | 115 | 99 | 115 | 94 | 140 | 115 |  |
| 25 | 146 | 124 | 152 | 131 | 145 | 125 | 180 | 150 |  |
| 35 | 180 | 154 | 188 | 162 | 175 | 150 | 215 | 180 |  |
| 50 | 219 | 187 | 228 | 197 | 210 | 175 | 255 | 215 |  |
| 70 | 279 | 238 | 291 | 251 | 260 | 215 | 315 | 265 |  |
| 95 | 338 | 289 | 354 | 304 | 310 | 260 | 380 | 315 |  |
| 120 | 392 | 335 | 410 | 353 | 355 | 300 | 430 | 360 |  |
| 150 | 451 | 386 | 472 | 406 | 400 | 335 | 480 | 405 |  |
| 185 | 515 | 441 | 539 | 463 | 455 | 380 | 540 | 460 |  |
| 240 | 607 | 520 | 636 | 546 | 520 | 440 | 630 | 530 |  |
| 300 | 698 | 599 | 732 | 628 | 590 | 495 | 700 | 590 |  |

76	Caledonian

Caledonian

Flame Retardant Power & Control Cables

www.caledonian-cables.co.uk	www.addison-cables.com

Voltage Drop (Per Amp Per Meter)

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 2 cables, | 3 or 4 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | single- | cables, |  |
| Conductor |  | 2-core |  | 2 cables, single-phase |  |  |  |  |  |  |  |  | 3 or 4 cables, 3-phase |  |  |  |  | phase | 3-phase |  |
| cross-sectional |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | a.c. | a.c. |  |
|  | cable d.c. |  |  |  |  |  | a.c. |  |  |  |  |  |  |  | a.c. |  |  |  |  |  |
| area |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | In ducts or | In ducts |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | or |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | in ground |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | in ground |  |
| 1 | 2 |  |  |  |  |  | 3 |  |  |  |  |  |  |  | 4 |  |  | 5 | 6 |  |
| mm2 | mV/A/m |  |  |  |  |  | mV/A/m |  |  |  |  |  |  |  | mV/A/m |  |  | mV/A/m | mV/A/m |  |
| 6 | 7.9 |  |  |  |  |  | 7.9 |  |  |  |  |  |  |  | 6.8 |  |  | 7.9 | 6.5 |  |
| 10 | 4.7 |  |  |  |  |  | 4.7 |  |  |  |  |  |  |  | 4.0 |  |  | 4.7 | 3.9 |  |
| 16 | 2.9 |  |  |  |  |  | 2.9 |  |  |  |  |  |  |  | 2.5 |  |  | 2.9 | 2.6 |  |
|  |  |  |  | r |  |  |  | x |  | z |  |  | r |  | x |  | z |  |  |  |
| 25 | 1.850 |  |  | 1.350 |  |  |  | 0.160 |  | 1.900 |  |  | 1.600 |  | 0.140 |  | 1.650 | 1.900 | 1.600 |  |
| 35 | 1.350 |  |  | 1.350 |  |  |  | 0.155 |  | 1.350 |  |  | 1.150 |  | 0.135 |  | 1.150 | 1.350 | 1.200 |  |
| 50 | 0.980 |  |  | 0.990 |  |  |  | 0.155 |  | 1.000 |  |  | 0.860 |  | 0.135 |  | 0.870 | 1.000 | 0.870 |  |
| 70 | 0.670 |  |  | 0.670 |  |  |  | 0.150 |  | 0.690 |  |  | 0.590 |  | 0.130 |  | 0.600 | 0.690 | 0.610 |  |
| 95 | 0.490 |  |  | 0.500 |  |  |  | 0.150 |  | 0.520 |  |  | 0.430 |  | 0.130 |  | 0.450 | 0.520 | 0.450 |  |
| 120 | 0.390 |  |  | 0.400 |  |  |  | 0.145 |  | 0.420 |  |  | 0.340 |  | 0.130 |  | 0.370 | 0.420 | 0.360 |  |
| 150 | 0.310 |  |  | 0.320 |  |  |  | 0.145 |  | 0.350 |  |  | 0.280 |  | 0.125 |  | 0.300 | 0.350 | 0.300 |  |
| 185 | 0.250 |  |  | 0.260 |  |  |  | 0.145 |  | 0.290 |  |  | 0.220 |  | 0.125 |  | 0.260 | 0.290 | 0.250 |  |
| 240 | 0.195 |  |  | 0.200 |  |  |  | 0.140 |  | 0.240 |  |  | 0.175 |  | 0.125 |  | 0.210 | 0.240 | 0.210 |  |
| 300 | 0.155 |  |  | 0.160 |  |  |  | 0.140 |  | 0.210 |  |  | 0.140 |  | 0.120 |  | 0.185 | 0.210 | 0.190 |  |
| 400 | 0.120 |  |  | 0.130 |  |  |  | 0.140 |  | 0.190 |  |  | 0.115 |  | 0.120 |  | 0.165 | 0.190 | 0.180 |  |
| Note : |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| r = conductor resistance at operating temperature |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| x = reactance |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| z = impedance |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 600/1000V |  | IECN60502-1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | Flame Retardancy** |  |  |  |  |  | Reduced |  | Fire Propagation** |  |  |  |  |  |  |  |  |
| Rated Voltage |  | Standard |  | NF C32-070-2.1(C2) |  |  |  |  |  | NF C32-070-2.2(C1) |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | IEC60332-1-2/EN50265-2-1 IEC60332-3-24/EN50266-2-4 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

ADDISON	77

ADDISON

TYPE CODES FOR FLame RETARDANT POWER & CONTROL CABLES

FGD A-B-C-D-E-F

F Conductor

U: Solid to IEC 60228 class 1

R: Stranded to IEC 60228 class 2

F: Stranded to IEC 60228 class 5

E Sheath

V: Thermoplastic PVC

D Screen

O: Overall aluminium tape screen

C: Overall copper tape screen

C Insulation

V: Thermoplastic PVC

B Voltage 05: 300/500V 07: 450/750V

1:  600/1000V

A Type

100: Single core unsheathed

200: 300/500V & 450/750V multicore 300: Single core sheathed

400: 600/1000V multicore

78	Caledonian