ADDISON

450/750V XLPE Insulated, PVC Sheathed Power Cables (Multicore)

FGD200 07RV-R (CU/XLPE/PVC 450/750V Class 2)

APPLICATION

The cables are mainly used in power stations, mass transit underground passenger systems, airports, petrochemical plants, hotels, hospitals, and high-rise buildings.

STANDARDS

Basic design adapted to IEC 60502-1

FIRE PERFORMANCE

Flame Retardance (Single Vertical EN 60332-1-2; IEC 60332-1-2; BS EN 60332-1-2; VDE Wire Test)** 0482-332-1 ; NBN C 30-004 (cat. F1); NF C32-070-2.1(C2);

CEI 20-35/1-2; EN 50265-2-1*; DIN VDE 0482-265-2-1*

| Reduced Fire Propagation | EN 60332-3-24 (cat. C); IEC 60332-3-24; BS EN 60332-3-24; |
| --- | --- |
| (Vertically-mounted bundled wires VDE 0482-332-3; NBN C 30-004 (cat. F2); NF C32-070-2.2(C1); |  |
| & cable test)** | CEI 20-22/3-4; EN 50266-2-4*; DIN VDE 0482-266-2-4 |

Note: Asterisk ** denotes that the standard compliance is optional, depending on the oxygen index of the PVC compound and the cable design.

VOLTAGE RATING

450/750V

CABLE CONSTRUCTION

Conductor: Plain annealed copper wire, stranded according to IEC(EN) 60228 class 2. Insulation: Extruded cross-linked XLPE compound.

Filler, binder (if any): PP, PET

Outer Sheath: Thermoplastic PVC compound. UV resistance, hydrocarbon resistance, oil resistance, anti rodent and anti termite properties can be offered as option. Compliance to fire performance standard (IEC 60332-1, IEC 60332-3, UL 1581, UL 1666 etc) depends on the oxygen index of the

24	Caledonian

Caledonian

Flame Retardant Power & Control Cables

www.caledonian-cables.co.uk	www.addison-cables.com

PVC compound and the overall cable design. LSPVC can also be provided upon request.

COLOUR CODE

Insulation Colour as per BS7671

|  | With Earth Conductor | Without Earth Conductor |
| --- | --- | --- |
| 2Cores | - | Brown, Blue |
| 3Cores | Yellow/Green, Brown, Blue | Brown, Gray, Black |
| 4Cores | Yellow/Green, Brown, Gray, Black | Brown, Gray, Black, Blue |
| 5Cores | Yellow/Green, Brown, Gray, Black, Blue | Brown, Gray, Black, Blue, Black |
| Above 5 Cores | Yellow/Green, Black Numbered | Black Numbered |

Sheath Colour: Black (other colors upon request)

Physical AND THERMAL PROPERTIES

Temperature range during operation: Max.90°C for XLPE

250°C in short-circuit for 5secs max.

Minimum bending radius: 6 x Overall Diameter

CONSTRUCTION PARAMETERS

|  | Conductor |  |  | FGD200 07RV-R |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| No. of | No./Nominal | Nominal | Nominal | Nominal | Nominal | Max.DC |  |  |
| Core X | Diameter of | Overall | Insulation | Sheath | Overall | resistance | Approx. |  |
| Cross |  | Diameter |  |  |  | of conductor | Weight |  |
| Section | Strands | Conductor | Thickness | Thickness | Diameter | @20°C |  |  |
| Noxmm2 | No./mm | mm | mm | mm | mm | Ω/km | kg/km |  |
| 7x1.0 | 7/0.44 | 1.32 | 0.7 | 1.3 | 11.6 | 18.1 | 210 |  |
| 7x1.5 | 7/0.53 | 1.59 | 0.7 | 1.3 | 12.5 | 12.1 | 258 |  |
| 7x2.5 | 7/0.67 | 2.01 | 0.7 | 1.3 | 13.8 | 7.41 | 347 |  |
| 12x1.5 | 7/0.53 | 1.59 | 0.7 | 1.4 | 16.5 | 12.1 | 413 |  |
| 12x2.5 | 7/0.67 | 2.01 | 0.7 | 1.5 | 18.3 | 7.41 | 561 |  |
| 19x1.5 | 7/0.53 | 1.59 | 0.7 | 1.5 | 19.3 | 12.1 | 609 |  |
| 19x2.5 | 7/0.67 | 2.01 | 0.7 | 1.6 | 21.6 | 7.41 | 836 |  |

Electrical PROPERTIES

Conductor Operating Temperature : 90°C

Ambient Temperature : 30°C

Current-Carrying Capacities (Amp)

ADDISON	25

ADDISON

|  | Reference |  | Reference |  |  |  |  |  | Reference Method 12 (free |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Method 4 |  |  |  |  |  | Reference |  |  | air) |  |  |
| Conductor |  |  | Method 3 |  |  |  |  |  |  |  |  |  |
|  | (enclosed |  |  |  |  |  | Method 11 (on a |  |  |  |  |  |
| cross- |  |  | (enclosed in |  | Reference Method |  |  |  |  |  |  |  |
| sectional | in conduit |  | conduit on |  | 1 (clipped direct) |  | perforated cable |  | Horizontal | Vertical |  |  |
| area | in thermally |  | a wall or in |  |  |  | tray, horizontal or |  | flat | flat | Trefoil |  |
|  | insulating wall |  |  |  |  |  | vertical) |  | spaced | spaced |  |  |
|  |  |  | trunking etc) |  |  |  |  |  |  |  |  |  |
|  | etc) |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | 2 cables, | 2 |  |  |
|  |  |  |  |  |  |  |  |  |  | cables, |  |  |
|  | 2 |  | 2 |  | 2 cables, | 3 or 4 | 2 cables, | 3 or 4 | single- | single- |  |  |
|  |  |  |  |  | single- | cables, | single- | cables, | phase |  |  |  |
|  | cables, | 3 or 4 | cables, | 3 or 4 |  |  |  |  |  | phase | 3 cables, |  |
|  |  |  |  |  | phase | 3-phase | phase | 3-phase | a.c. or |  |  |  |
|  | single- | cables, | single- | cables, |  |  |  |  |  | a.c. or | trefoil |  |
|  | phase | 3-phase | phase | 3-phase | a.c. or | a.c. flat | a.c. or | a.c. flat | d.c. | d.c. | 3-phase |  |
|  | a.c. or | a.c. | a.c. or | a.c. | d.c. flat | and | d.c. or | and | or 3 c | or 3 | a.c. |  |
|  | d.c. |  | d.c |  | and | touching | flat and | touching | ables | cables |  |  |
|  |  |  |  |  | touching | or trefoil | touching | or trefoil | three |  |  |  |
|  |  |  |  |  |  |  |  |  |  | three |  |  |
|  |  |  |  |  |  |  |  |  | phase |  |  |  |
|  |  |  |  |  |  |  |  |  |  | phase |  |  |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 |  |
| mm2 | A | A | A | A | A | A | A | A | A | A | A |  |
| 1.0 | 13 | - | - | - | 15 | - | - | - | - | - | - |  |
| 1.5 | 18 | 17 | 22 | 19 | 25 | 23 | - | - | - | - | - |  |
| 2.5 | 24 | 23 | 30 | 26 | 34 | 31 | - | - | - | - | - |  |

Voltage Drop (Per Amp Per Meter)

| Nominal |  |  |  |  |  |  |  | 2 cables, single-phase a.c. |  |  |  |  |  |  |  |  |  |  |  | 3 or 4 cables, 3-phase a.c. |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  | Ref. Methods 3 |  |  |  |  | Ref. Methods 1 |  |  |  |  | Ref. Methods 3 |  |  |  |  | Ref. Methods 1 and |  |
| Cross |  |  | 2 cables |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Ref. Methods 1, |  |  |
|  |  |  |  |  |  |  |  | and 4 (enclosed |  |  |  |  | and 11 (clipped |  |  |  |  | and 4 (enclosed |  |  |  |  | 11 |  |
| Section |  |  |  |  | d.c. |  |  | in conduit etc, |  |  |  | direct or on trays |  |  |  |  |  | in conduit etc, |  |  |  | 11 and 12 (in |  |  |
|  |  | Area |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | (Flat and touching) |  |
|  |  |  |  |  |  |  |  | in or on a wall) |  |  |  |  | touching) |  |  |  |  | in or on a wall) |  |  |  | trefoil) |  |  |
| 1 |  |  |  | 2 |  |  |  | 3 |  |  | 4 |  |  |  |  |  |  | 5 |  |  |  | 6 | 7 |  |
|  |  | mm2 |  | mV/A/m |  |  |  | mV/A/m |  |  |  |  | mV/A/m |  |  |  |  |  | mV/A/m |  |  | mV/A/m | mV/A/m |  |
| 1.0 |  |  |  | 46 |  |  |  | 46 |  |  | - |  |  |  |  |  |  | - |  |  |  | - | - |  |
| 1.5 |  |  |  | 31 |  |  |  | 31 |  |  | 27 |  |  |  |  |  |  | 27 |  |  |  | 27 | 27 |  |
| 2.5 |  |  |  | 19 |  |  |  | 19 |  |  | 16 |  |  |  |  |  |  | 16 |  |  |  | 16 | 16 |  |
|  |  | 450/750V |  |  |  |  |  | IECN60502-1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  | Flame Retardancy** | Reduced Fire Propagation** |  |
| --- | --- | --- | --- | --- |
| Rated Voltage | Standard | NF C32-070-2.1(C2) | NF C32-070-2.2(C1) |  |
|  |  | IEC60332-1-2/EN50265-2-1 | IEC60332-3-24/EN50266-2-4 |  |

26	Caledonian