BS 6883&BS 7917 Caledonian Offshore & Marine Cables

Flame Retardant Instrumentation & Control Cables

www.caledonian-cables.co.uk

150/250V HF-EPR Insulated, SW2/SW4 Sheathed, Collectively Screened Unarmoured Flame Retardant Instrumentation & Control Cables

Application

These elastomeric insulated cables are designed for fixed wiring in ships and on mobile offshore units, suitable for use in instrumentation, lighting and control circuits.

Standards

	BS 6883

- IEC 60332-3A Flame retardant

	IEC 60754-1; IEC 60754-2

Corrosivity

- IEC 61034-2 Smoke density

- Cold bend and impact (-40°C) (on request)

- CSA C22.2 No. 38-95 (on request)

Construction

Stranded Tinned Copper Conductor HF-EPR GP4 Insulation

Aluminium/Polyester Tape + Drain Wire SW4/SW2 Sheath

- Conductor: Tinned copper wire stranded circular cl. 2 BS 6360/IEC 60228.

- Insulation: HF-EPR GP4 according to BS 7655 1.2.

- Lay-up: Pairs, triples.

- Collective Screen: Aluminium/polyester tape + drain wire tinned copper.

- Sheath: Halogen free thermosetting compound SW4 according to BS 7655 2.6 or reduced halogen thermosetting compound SW2 according to BS 7655 2.6.

Mechanical and Thermal Properties

Minimum Internal Bending Radius: 8×OD Temperature Range: -40℃ ~ +90℃

32	ADDISON	www.addison-cables.com

BS 6883&BS 7917 Caledonian Offshore & Marine Cables

Flame Retardant Instrumentation & Control Cables

www.caledonian-cables.co.uk

Dimensions and Weight

| Construction No. of cores×Cross section(mm²) | Nominal Insulation Thickness mm | Nominal Sheath Thickness mm | Minimum Overall Diameter mm | Maximum Overall Diameter mm | Approx. Weight kg/km |
| --- | --- | --- | --- | --- | --- |
| Multipair |  |  |  |  |  |
| 3×2×0.75 | 0.8 | 1.2 | 12.6 | 14.5 | 175 |
| 7×2×0.75 | 0.8 | 1.4 | 16.6 | 18.7 | 330 |
| 12×2×0.75 | 0.8 | 1.6 | 21.7 | 24.2 | 530 |
| 20×2×0.75 | 0.8 | 1.8 | 27.3 | 30.1 | 830 |
| 27×2×0.75 | 0.8 | 1.9 | 31.1 | 34.2 | 1070 |
| 37×2×0.75 | 0.8 | 2.1 | 34.4 | 37.7 | 1430 |
| 3×2×1 | 0.8 | 1.2 | 13.3 | 15.3 | 185 |
| 7×2×1 | 0.8 | 1.4 | 17.6 | 19.8 | 360 |
| 12×2×1 | 0.8 | 1.6 | 23.1 | 25.7 | 590 |
| 20×2×1 | 0.8 | 1.8 | 29.1 | 31.9 | 920 |
| 27×2×1 | 0.8 | 2.0 | 33.3 | 36.6 | 1220 |
| 37×2×1 | 0.8 | 2.2 | 36.9 | 40.3 | 1630 |
| Multitriple |  |  |  |  |  |
| 3×3×0.75 | 0.8 | 1.3 | 14.2 | 16.2 | 230 |
| 7×3×0.75 | 0.8 | 1.4 | 19.4 | 21.9 | 440 |
| 12×3×0.75 | 0.8 | 1.7 | 24.2 | 26.8 | 730 |
| 3×3×1 | 0.8 | 1.3 | 15.1 | 17.1 | 260 |
| 7×3×1 | 0.8 | 1.5 | 20.9 | 23.4 | 510 |
| 12×3×1 | 0.8 | 1.7 | 25.8 | 28.5 | 840 |

www.addison-cables.com

ADDISON	33