BS 6883&BS 7917 Caledonian Offshore & Marine Cables

LV Flame Retardant Power & Control Cables

www.caledonian-cables.co.uk

  - /1kV HF-EPR Insulated, SW2/SW4 Sheathed Unarmoured Flame Retardant Power & Control Cables

Application

These elastomeric insulated cables are designed for fixed wiring in ships and on mobile offshore units, suitable for use in power and control applications.

Standards

	BS 6883

    - IEC 60332-3A Flame retardant

	IEC 60754-1; IEC 60754-2

Corrosivity

    - IEC 61034-2 Smoke density

    - Cold bend and impact (-40°C) (on request)

    - CSA C22.2 No. 38-95 (on request)

Construction

Stranded Tinned Copper Conductor HF-EPR GP4 Insulation

SW2/SW4 Outer Sheath

    - Conductor: Tinned copper wire stranded circular cl. 2 BS 6360/IEC 60228.

    - Insulation: HF-EPR GP4 according to BS 7655 1.2.

    - Sheath: Halogen free thermosetting compound SW4 according to BS 7655 2.6 or reduced halogen thermosetting compound SW2 according to BS 7655 2.6.

Mechanical and Thermal Properties

Minimum Internal Bending Radius: 6×OD (OD>25mm); 4×OD (OD ≤25mm) Temperature Range: -40℃ ~ +90℃

18	ADDISON	www.addison-cables.com

BS 6883&BS 7917 Caledonian Offshore & Marine Cables

LV Flame Retardant Power & Control Cables

www.caledonian-cables.co.uk

Dimensions and Weight

Single core cables

| Construction No. of cores×Cross section(mm²) | Nominal Insulation Thickness mm | Nominal Sheath Thickness mm | Minimum Overall Diameter mm | Maximum Overall Diameter mm | Approx. Weight kg/km |
| --- | --- | --- | --- | --- | --- |
| 1×4 | 1.0 | 1.0 | 6.3 | 7.6 | 85 |
| 1×6 | 1.0 | 1.0 | 6.8 | 8.1 | 120 |
| 1×10 | 1.0 | 1.0 | 7.7 | 9.1 | 165 |
| 1×16 | 1.0 | 1.1 | 8.9 | 10.3 | 230 |
| 1×25 | 1.2 | 1.2 | 11.1 | 12.8 | 345 |
| 1×35 | 1.2 | 1.2 | 12.0 | 13.7 | 445 |
| 1×50 | 1.4 | 1.3 | 13.7 | 15.5 | 600 |
| 1×70 | 1.4 | 1.3 | 15.5 | 17.4 | 810 |
| 1×95 | 1.6 | 1.4 | 17.7 | 19.8 | 1100 |
| 1×120 | 1.6 | 1.5 | 19.6 | 22.0 | 1360 |
| 1×150 | 1.8 | 1.6 | 21.6 | 24.2 | 1650 |
| 1×185 | 2.0 | 1.7 | 24.0 | 26.6 | 2070 |
| 1×240 | 2.2 | 1.8 | 27.1 | 29.9 | 2670 |
| 1×300 | 2.4 | 1.9 | 30.0 | 33.2 | 3340 |

Multicore cables

| Construction No. of cores×Cross section(mm²) | Nominal Insulation Thickness mm | Nominal Sheath Thickness mm | Minimum Overall Diameter mm | Maximum Overall Diameter mm | Approx. Weight kg/km |
| --- | --- | --- | --- | --- | --- |
| 2×1 | 0.8 | 1.0 | 7.5 | 8.8 | 100 |
| 2×1.5 | 0.8 | 1.1 | 8.2 | 9.6 | 125 |
| 2×2.5 | 0.8 | 1.1 | 9.0 | 10.4 | 160 |
| 2×4 | 1.0 | 1.2 | 11.0 | 12.7 | 235 |
| 2×6 | 1.0 | 1.2 | 12.1 | 13.8 | 300 |
| 2×10 | 1.0 | 1.3 | 14.1 | 15.9 | 415 |
| 2×16 | 1.0 | 1.4 | 16.3 | 18.3 | 590 |
| 2×25 | 1.2 | 1.5 | 20.4 | 22.9 | 890 |
| 2×35 | 1.2 | 1.6 | 22.4 | 24.9 | 1150 |
| 2×50 | 1.4 | 1.7 | 25.7 | 28.4 | 1570 |
| 2×70 | 1.4 | 1.9 | 29.6 | 32.7 | 2140 |
| 2×95 | 1.6 | 2.1 | 34.1 | 37.4 | 2930 |
| 2×120 | 1.6 | 2.2 | 37.7 | 41.1 | 3600 |
| 3×1 | 0.8 | 1.1 | 8.2 | 9.5 | 110 |
| 3×1.5 | 0.8 | 1.1 | 8.7 | 10.1 | 150 |
| 3×2.5 | 0.8 | 1.1 | 9.6 | 11.0 | 190 |
| 3×4 | 1.0 | 1.2 | 11.7 | 13.4 | 280 |
| 3×6 | 1.0 | 1.2 | 12.9 | 14.7 | 370 |
| 3×10 | 1.0 | 1.3 | 15.0 | 17.0 | 505 |
| 3×16 | 1.0 | 1.4 | 17.4 | 19.4 | 750 |

www.addison-cables.com

ADDISON	19

BS 6883&BS 7917 Caledonian Offshore & Marine Cables

LV Flame Retardant Power & Control Cables

www.caledonian-cables.co.uk

| Construction No. of cores×Cross section(mm²) | Nominal Insulation Thickness mm | Nominal Sheath Thickness mm | Minimum Overall Diameter mm | Maximum Overall Diameter mm | Approx. Weight kg/km |
| --- | --- | --- | --- | --- | --- |
| 3×25 | 1.2 | 1.6 | 22.0 | 24.6 | 1150 |
| 3×35 | 1.2 | 1.7 | 24.1 | 26.7 | 1490 |
| 3×50 | 1.4 | 1.8 | 27.7 | 30.5 | 2030 |
| 3×70 | 1.4 | 2.0 | 31.8 | 35.1 | 2790 |
| 3×95 | 1.6 | 2.2 | 36.7 | 40.1 | 3820 |
| 3×120 | 1.6 | 2.3 | 40.5 | 44.4 | 4710 |
| 3×150 | 1.8 | 2.5 | 44.9 | 49.0 | 5710 |
| 3×185 | 2.0 | 2.7 | 50.1 | 54.6 | 7180 |
| 3×240 | 2.2 | 2.9 | 56.7 | 61.5 | 9310 |
| 3×300 | 2.4 | 3.2 | 63.1 | 68.6 | 10860 |
| 4×1 | 0.8 | 1.1 | 8.9 | 10.3 | 140 |
| 4×1.5 | 0.8 | 1.1 | 9.5 | 10.9 | 175 |
| 4×2.5 | 0.8 | 1.1 | 10.5 | 12.1 | 225 |
| 4×4 | 1.0 | 1.2 | 12.9 | 14.6 | 340 |
| 4×6 | 1.0 | 1.3 | 14.4 | 16.2 | 465 |
| 4×10 | 1.0 | 1.4 | 16.7 | 18.7 | 640 |
| 4×16 | 1.0 | 1.5 | 19.4 | 21.8 | 960 |
| 4×25 | 1.2 | 1.7 | 24.5 | 27.1 | 1550 |
| 4×35 | 1.2 | 1.8 | 26.8 | 29.5 | 1920 |
| 4×50 | 1.4 | 1.9 | 30.8 | 34.0 | 2600 |
| 4×70 | 1.4 | 2.1 | 35.4 | 38.8 | 3570 |
| 4×95 | 1.6 | 2.3 | 40.8 | 44.7 | 4900 |
| 4×120 | 1.6 | 2.5 | 45.2 | 49.3 | 6070 |
| 4×150 | 1.8 | 2.7 | 50.1 | 54.7 | 7360 |
| 4×185 | 2.0 | 2.9 | 55.8 | 60.7 | 9260 |
| 4×240 | 2.2 | 3.2 | 63.4 | 68.9 | 12030 |
| 5×1.5 | 0.8 | 1.1 | 10.4 | 12.0 | 200 |
| 7×1.5 | 0.8 | 1.2 | 11.5 | 13.2 | 255 |
| 12×1.5 | 0.8 | 1.3 | 15.2 | 17.2 | 405 |
| 19×1.5 | 0.8 | 1.4 | 18.0 | 20.1 | 600 |
| 27×1.5 | 0.8 | 1.6 | 21.9 | 24.5 | 850 |
| 37×1.5 | 0.8 | 1.7 | 24.7 | 27.3 | 1120 |
| 5×2.5 | 0.8 | 1.2 | 11.7 | 13.3 | 270 |
| 7×2.5 | 0.8 | 1.2 | 12.7 | 14.4 | 335 |
| 12×2.5 | 0.8 | 1.4 | 17.1 | 19.1 | 550 |
| 19×2.5 | 0.8 | 1.5 | 20.2 | 22.7 | 830 |

20	ADDISON	www.addison-cables.com