ADDISON

Flame Retardant CAT5e Data Cables

FTX-CAT5e U/UTP4P24

FTX-CAT5e f/UTP4P24

FTX-CAT5e sf/UTP4P24

APPLICATION

Cat5E is a cable standard for Gigabit Ethernet and other network protocol, suitable for basic voice and data installations up to 100 MHz. In addition, these cables can be offered with copper wire braid armoured & flame retardant outer sheath, providing additional mechanically protection still maintaining the flexibility of the cable.

STANDARDS

Basic design adapted to EN50173

FIRE PERFORMANCE

| Flame Retardance (Single Vertical | EN 60332-1-2; IEC 60332-1-2; BS EN 60332-1-2; VDE |  |
| --- | --- | --- |
|  | 0482-332-1 ; NBN C 30-004 (cat. F1); NF C32-070-2.1(C2); |  |
| Wire Test) | CEI 20-35/1-2; EN 50265-2-1*; DIN VDE 0482-265-2-1* |  |
| Reduced Fire Propagation | EN 60332-3-24 (cat. C); IEC 60332-3-24; BS EN 60332-3-24; |  |
| (Vertically-mounted bundled wires | VDE 0482-332-3; NBN C 30-004 (cat. F2); NF C32-070-2.2(C1); |  |
| & cable test) | CEI 20-22/3-4; EN 50266-2-4*; DIN VDE 0482-266-2-4 |  |
| Halogen Free | IEC 60754-1; EN 50267-2-1; DIN VDE 0482-267-2-1; |  |
|  | CEI 20-37/2-1 ; BS 6425-1* |  |
| No Corrosive Gas Emission | IEC 60754-2; EN 50267-2-2; DIN VDE 0482-267-2-2; |  |
|  | CEI 20-37/2-2 ; BS 6425-2* |  |
| Minimum Smoke Emission | IEC 61034-1&2; EN 61034 -1&2; DIN VDE 0482-1034-1&2; |  |
|  | CEI 20-37/3-1&2; EN 50268-1&2*; BS 7622-1&2* |  |
| No Toxic gases | NES 02-713; NF C 20-454 |  |

Note: Asterisk * denotes superseded standard.

104	Caledonian

Caledonian

Flame Retardant Data Cables

www.caledonian-cables.co.uk	www.addison-cables.com

VOLTAGE RATING

60V

CABLE CONSTRUCTION

Conductors: 24AWG solid bare copper.

Insulation: HDPE.

Twinning: Two coloured insulated conductors twisted together to form a pair.

Outer Sheath: Thermoplastic LSZH compound type LTS3 as per BS 7655-6.1 (Thermosetting LSZH compound type SW2-SW4 as per BS 7655:section 2.6 can be offered.). UV resistance, hydrocarbon resistance, oil resistance, anti rodent and anti termite properties can be offered as option.

Cat5E F/UTP: These cables have collective shielding of aluminium/Polyester tape with drain wire. Cat5E SF/UTP: These cables have double collective shieldings of aluminium/Polyester tape & copper wire braid.

Physical AND THERMAL PROPERTIES

Temperature range: -30°C ~ +75°C

Minimum bending radius during installation (mobile state): 8 x Overall Diameter

Minimum bending radius during operation (fixed state):4 x Overall Diameter

Electrical Properties

| AWG |  | 24 |
| --- | --- | --- |
| Nominal Conductor Diameter | mm | 0.5/0.51/0.53 |
| Maximum DC Resistant@20°C | Ω/100m | 9.38 |
| Maximum DCR Unbalance | % | 5 |
| Maximum Mutual Capacitance | pF/m | 55.8 |
| Maximum Capacitance Unbalance | pF/100m | 330 |
| Characteristic Impedance@1-100MHz | Ω | 100+/-15 |
| Maximum Propagation Delay Skew | ns/100m | 45 |

Transmission Properties

| FREQ | Maximum | Minimum | Minimum | Minimum | Minimum | Minimum |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Attenuation | NEXT | PSNEXT | ELFEXT | PSELFEXT | RL |  |
| MHz |  |  |  |  |  |  |  |
|  | dB/100m | dB | dB | dB/100m | dB/100m | dB |  |
| 0.772 | 1.8 | 67.0 | 64.0 | 66.0 | 63.0 | — |  |
| 1 | 2.0 | 65.3 | 62.3 | 63.8 | 60.8 | 20.0 |  |
| 4 | 4.1 | 56.3 | 53.3 | 51.7 | 48.7 | 23.0 |  |
| 8 | 5.8 | 51.8 | 48.8 | 45.7 | 42.7 | 24.5 |  |
| 10 | 6.5 | 50.3 | 47.3 | 43.8 | 40.8 | 25.0 |  |
| 16 | 8.2 | 47.3 | 44.3 | 39.7 | 36.7 | 25.0 |  |

ADDISON   105