Caledonian

Flame Retardant Data Cables

www.caledonian-cables.co.uk	www.addison-cables.com

Flame Retardant CAT6 Data Cables

FTX-CAT6 U/UTP4P23

FTX-CAT6 F/UTP4P23

FTX-CAT6 SF/FTP4P23

APPLICATION

Cat6 Cable is a cable standard for Gigabit Ethernet and other network protocol, suitable for 10BaseT, 100BaseTx & 1000BaseT (Gigabit Ethernet) application. In addition, these cables are with copper wire braid armoured & flame retardant mud resistant outer sheath, providing additional mechanically protection still maintaining the flexibility of the cable.

STANDARDS

Basic design adapted to EN50173

FIRE PERFORMANCE

| Flame Retardance (Single Vertical | EN 60332-1-2; IEC 60332-1-2; BS EN 60332-1-2; VDE |  |
| --- | --- | --- |
|  | 0482-332-1 ; NBN C 30-004 (cat. F1); NF C32-070-2.1(C2); |  |
| Wire Test) | CEI 20-35/1-2; EN 50265-2-1*; DIN VDE 0482-265-2-1* |  |
| Reduced Fire Propagation | EN 60332-3-24 (cat. C); IEC 60332-3-24; BS EN 60332-3-24; |  |
| (Vertically-mounted bundled wires | VDE 0482-332-3; NBN C 30-004 (cat. F2); NF C32-070-2.2(C1); |  |
| & cable test) | CEI 20-22/3-4; EN 50266-2-4*; DIN VDE 0482-266-2-4 |  |
| Halogen Free | IEC 60754-1; EN 50267-2-1; DIN VDE 0482-267-2-1; |  |
|  | CEI 20-37/2-1 ; BS 6425-1* |  |
| No Corrosive Gas Emission | IEC 60754-2; EN 50267-2-2; DIN VDE 0482-267-2-2; |  |
|  | CEI 20-37/2-2 ; BS 6425-2* |  |
| Minimum Smoke Emission | IEC 61034-1&2; EN 61034 -1&2; DIN VDE 0482-1034-1&2; |  |
|  | CEI 20-37/3-1&2; EN 50268-1&2*; BS 7622-1&2* |  |
| No Toxic gases | NES 02-713; NF C 20-454 |  |

Note: Asterisk * denotes superseded standard.

VOLTAGE RATING

60V

ADDISON   111

ADDISON

CABLE CONSTRUCTION

Conductors: 23AWG solid bare copper.

Insulation: HDPE.

Twinning: Two coloured insulated conductors twisted together to form a pair.

Outer Sheath: Thermoplastic LSZH compound type LTS3 as per BS 7655-6.1 (Thermosetting LSZH compound type SW2-SW4 as per BS 7655:section 2.6 can be offered.). UV resistance, hydrocarbon resistance, oil resistance, anti rodent and anti termite properties can be offered as option.

Cat6 F/UTP: These cables have collective shielding of aluminium/Polyester tape with drain wire. Cat6 SF/UTP: These cables have double collective shieldings of aluminium/Polyester tape & copper wire braid with drain wire.

Physical AND THERMAL PROPERTIES

Temperature range: -30°C ~ +75°C

Minimum bending radius during installation (mobile state): 8 x Overall Diameter

Minimum bending radius during operation (fixed state):4 x Overall Diameter

Electrical Properties

|  |  | AWG |  |  |  |  |  |  | 23 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Nominal Conductor Diameter |  |  |  |  | mm |  | 0.56/0.57/0.58 |  |  |  |
|  |  | Maximum DC Resistant@20°C |  |  |  |  | Ω/100m |  | 9.38 |  |  |  |
|  |  | Maximum DCR Unbalance |  |  |  |  | % |  | 3 |  |  |  |
|  |  | Maximum Mutual Capacitance |  |  |  |  | pF/m |  | 5.8 |  |  |  |
|  |  | Maximum Capacitance Unbalance |  |  |  |  | pF/100m |  | 30 |  |  |  |
|  |  | Characteristic Impedance@1-100MHz |  |  |  |  | Ω |  | 100+/-15 |  |  |  |
|  |  | Maximum Propagation Delay Skew |  |  |  |  | ns/100m |  | 18 |  |  |  |
|  | Transmission Properties |  |  |  |  |  |  |  |  |  |  |  |
|  |  | FREQ | Maximum |  | Minimum |  | Minimum | Minimum |  | Minimum | Minimum |  |
|  |  |  | Attenuation |  | NEXT |  | PSNEXT | ELFEXT |  | PSELFEXT | RL |  |
|  |  | MHz |  |  |  |  |  |  |  |  |  |  |
|  |  |  | dB/100m |  | dB |  | dB | dB/100m |  | dB/100m | dB |  |
|  |  | 0.772 | 1.8 |  | 76.0 |  | 74. | 70.0 |  | 67.0 | — |  |
|  |  | 1 | 2.0 |  | 74.3 |  | 72.3 | 67.8 |  | 64.8 | 20.0 |  |
|  |  | 4 | 3.8 |  | 65.3 |  | 63.3 | 55.7 |  | 52.7 | 23.0 |  |
|  |  | 8 | 5.3 |  | 60.8 |  | 58.8 | 49.7 |  | 46.7 | 24.5 |  |
|  |  | 10 | 6.0 |  | 59.3 |  | 57.3 | 47.8 |  | 44.8 | 25.0 |  |
|  |  | 16 | 7.6 |  | 56.3 |  | 54.3 | 43.7 |  | 40.7 | 25.0 |  |
|  |  | 20 | 8.5 |  | 54.8 |  | 52.8 | 41.7 |  | 38.7 | 25.0 |  |
|  |  | 25 | 9.5 |  | 53.3 |  | 51.3 | 39.8 |  | 36.8 | 24.3 |  |
|  |  | 31.25 | 10.7 |  | 51.9 |  | 49.9 | 37.9 |  | 34.9 | 23.6 |  |
|  |  | 62.5 | 15.4 |  | 47.4 |  | 45.4 | 31.8 |  | 28.8 | 21.5 |  |
| 112 | Caledonian |  |  |  |  |  |  |  |  |  |  |  |