ADDISON

Flame Retardant Individual and Overall Screened Instrumentation Cables (Multipair)

RE-2X(St)H Pimf

APPLICATION

The unarmoured LSZH versions (Part 1 Type 1) cables are generally use for indoor installation and suitable for wet and damp areas. Generally used within industrial process manufacturing plants for communication, data and voice transmission signals and services, Also used for the interconnection of electrical equipment and instruments, the LSZH sheath can reduce toxic smoke and fume emission.

STANDARDS

Basic design adapted to BS 5308 Part 1 Type 1

FIRE PERFORMANCE

| Flame Retardance (Single Vertical | EN 60332-1-2; IEC 60332-1-2; BS EN 60332-1-2; VDE |  |
| --- | --- | --- |
|  | 0482-332-1 ; NBN C 30-004 (cat. F1); NF C32-070-2.1(C2); |  |
| Wire Test) | CEI 20-35/1-2; EN 50265-2-1*; DIN VDE 0482-265-2-1* |  |
| Reduced Fire Propagation | EN 60332-3-24 (cat. C); IEC 60332-3-24; BS EN 60332-3-24; |  |
| (Vertically-mounted bundled wires | VDE 0482-332-3; NBN C 30-004 (cat. F2); NF C32-070-2.2(C1); |  |
| & cable test) | CEI 20-22/3-4; EN 50266-2-4*; DIN VDE 0482-266-2-4 |  |
| Halogen Free | IEC 60754-1; EN 50267-2-1; DIN VDE 0482-267-2-1; |  |
|  | CEI 20-37/2-1 ; BS 6425-1* |  |
| No Corrosive Gas Emission | IEC 60754-2; EN 50267-2-2; DIN VDE 0482-267-2-2; |  |
|  | CEI 20-37/2-2 ; BS 6425-2* |  |
| Minimum Smoke Emission | IEC 61034-1&2; EN 61034 -1&2; DIN VDE 0482-1034-1&2; |  |
|  | CEI 20-37/3-1&2; EN 50268-1&2*; BS 7622-1&2* |  |
| No Toxic gases | NES 02-713; NF C 20-454 |  |

Note: Asterisk * denotes superseded standard.

VOLTAGE RATING

300/500V

90	Caledonian

Caledonian

Flame Retardant Instrumentation Cables

www.caledonian-cables.co.uk	www.addison-cables.com

CABLE CONSTRUCTION

Conductor: Annealed or tinned copper, sizes: 0.5mm² and 0.75mm² mulitistranded(Class 5), 0.5 mm², 1.0 mm² solid(Class 1), 1.5mm² or 2.5mm², multistranded(Class 2) to BS6360

Insulation: XLPE (Cross Linked Polyethylene), or PE (optional)

Pairs: Two insulated conductors uniformly twisted together with a lay not exceeding 100mm Individual Screen: Aluminium/polyester tape is applied over each pair metallic side down in contact with tinned copper drain wire, 0.5mm²

Binder tape: PETP transparent tape

Overall Screen: Aluminium/polyester tape is applied over the laid up pairs metallic side down in contact with tinned copper drain wire, 0.5mm²

Outer Sheath: Thermoplastic LSZH compound type LTS3 as per BS 7655-6.1 (Thermosetting LSZH compound type SW2-SW4 as per BS 7655-2.6 can be offered.). UV resistance, hydrocarbon resistance, oil resistance, anti rodent and anti termite properties can be offered as option.

COLOUR CODE

Insulation Colour: See technical information

Outer sheath: Black or blue

Physical AND THERMAL PROPERTIES

Maximum Operating temperature: -20˚C - + 90˚C( fixed installation) 0˚C - +50˚C(during operation)

Minimum bending radius: 5 x Overall Diameter

Electrical Properties

| Conductor Area Size | mm 2 | 0.5 | 0.5 | 0.75 | 1.0 | 1.5 |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Conductor Stranding | No. x mm | 1 x 0.8 | 16 x 0.2 | 24 x 0.2 | 1 x 1.13 | 7 x 0.53 |  |
| Conductor resistance max | ohm/km | 36.8 | 39.7 | 26.5 | 18.2 | 12.3 |  |
| Insulation resistance min | Gohm/km | 5 | 5 | 5 | 5 | 5 |  |
| Capacitance unbalance at 1 | pF/250m |  |  | 250 |  |  |  |
| kHz(pair to pair screen) |  |  |  |  |  |  |  |
| Max. Mutual Capacitance @ 1 |  |  |  |  |  |  |  |
| kHz forNon OS or OS cables | pF/m | 115 | 115 | 115 | 115 | 115 |  |
| (except one-pair and two- |  |  |  |  |  |  |  |
| pairs) |  |  |  |  |  |  |  |
| Max. Mutual Capacitance @ |  |  |  |  |  |  |  |
| 1 kHz IS/OS cables (include 1 | pF/m | 75 | 75 | 75 | 75 | 75 |  |
| pair and 2 pair) |  |  |  |  |  |  |  |
| Max. L/R Ratio for adjacent | μH/ohm | 25 | 25 | 25 | 25 | 40 |  |
| cores(Inductance/Resistance) |  |  |  |  |  |  |  |

ADDISON	91

ADDISON

| Test voltage | Core to core | V | 1000 | 1000 | 1000 | 1000 | 1000 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Core to screen | V | 1000 | 1000 | 1000 | 1000 | 1000 |  |
| Rated voltage max |  | V | 300/500 | 300/500 | 300/500 | 300/500 | 300/500 |  |

CONSTRUCTION PARAMETERS

|  | No./ | Nominal Conductor | Nominal | Nominal | Nominal |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Nominal |  |  |  |  | Approx. |  |
|  |  |  | Insulation | Sheath | Overall |  |  |
| Number | Diameter | Cross- |  |  |  |  |  |
|  |  |  |  |  |  | Weight |  |
| of Pairs | of | Section Area | Thickness | Thickness | Diameter |  |  |
|  | Strands |  |  |  |  |  |  |
|  | No./mm | mm2 | mm | mm | mm | kg/km |  |
| 2 | 1/0.8 | 0.5 | 0.5 | 0.9 | 9.7 | 95 |  |
| 5 | 1/0.8 | 0.5 | 0.5 | 1.2 | 13 | 180 |  |
| 10 | 1/0.8 | 0.5 | 0.5 | 1.2 | 16.9 | 310 |  |
| 15 | 1/0.8 | 0.5 | 0.5 | 1.3 | 19.7 | 440 |  |
| 20 | 1/0.8 | 0.5 | 0.5 | 1.3 | 22.3 | 560 |  |
| 30 | 1/0.8 | 0.5 | 0.5 | 1.5 | 27.1 | 820 |  |
| 50 | 1/0.8 | 0.5 | 0.5 | 2 | 35 | 1370 |  |
| 2 | 16/0.2 | 0.5 | 0.6 | 1.1 | 11.2 | 110 |  |
| 5 | 16/0.2 | 0.5 | 0.6 | 1.2 | 14.5 | 250 |  |
| 10 | 16/0.2 | 0.5 | 0.6 | 1.3 | 19.3 | 480 |  |
| 15 | 16/0.2 | 0.5 | 0.6 | 1.5 | 22.6 | 570 |  |
| 20 | 16/0.2 | 0.5 | 0.6 | 1.5 | 25.7 | 780 |  |
| 30 | 16/0.2 | 0.5 | 0.6 | 1.7 | 31 | 1020 |  |
| 50 | 16/0.2 | 0.5 | 0.6 | 2.2 | 39.9 | 1680 |  |
| 2 | 1/1.13 | 1 | 0.6 | 1.1 | 11.9 | 200 |  |
| 5 | 1/1.13 | 1 | 0.6 | 1.2 | 15.4 | 290 |  |
| 10 | 1/1.13 | 1 | 0.6 | 1.3 | 20.5 | 580 |  |
| 15 | 1/1.13 | 1 | 0.6 | 1.5 | 24.1 | 780 |  |
| 20 | 1/1.13 | 1 | 0.6 | 1.7 | 27.7 | 1010 |  |
| 30 | 1/1.13 | 1 | 0.6 | 2 | 33.7 | 1430 |  |
| 50 | 1/1.13 | 1 | 0.6 | 2.2 | 42.5 | 2360 |  |
| 2 | 7/0.53 | 1.5 | 0.6 | 1.2 | 13.6 | 250 |  |
| 5 | 7/0.53 | 1.5 | 0.6 | 1.3 | 17.7 | 460 |  |
| 10 | 7/0.53 | 1.5 | 0.6 | 1.5 | 23.9 | 760 |  |
| 15 | 7/0.53 | 1.5 | 0.6 | 1.7 | 28 | 1020 |  |
| 20 | 7/0.53 | 1.5 | 0.6 | 2 | 31.7 | 1350 |  |

92	Caledonian