ADDISON

600/1000V LSZH Insulated, Non-sheathed Power Cables (Single Core)

FTX300 1Z1-R (CU/LSZH 600/1000V Class 2)

APPLICATION

The cables is mainly used in power stations, mass transit underground passenger systems, airports, petrochemical plants, hotels, hospitals, and high-rise buildings.

STANDARDS

Basic design adapted to BS 7211

FIRE PERFORMANCE

| Flame Retardance (Single Vertical | EN 60332-1-2; IEC 60332-1-2; BS EN 60332-1-2; VDE |  |
| --- | --- | --- |
|  | 0482-332-1 ; NBN C 30-004 (cat. F1); NF C32-070-2.1(C2); |  |
| Wire Test) | CEI 20-35/1-2; EN 50265-2-1*; DIN VDE 0482-265-2-1* |  |
| Reduced Fire Propagation | EN 60332-3-24 (cat. C); IEC 60332-3-24; BS EN 60332-3-24; |  |
| (Vertically-mounted bundled wires | VDE 0482-332-3; NBN C 30-004 (cat. F2); NF C32-070-2.2(C1); |  |
| & cable test) | CEI 20-22/3-4; EN 50266-2-4*; DIN VDE 0482-266-2-4 |  |
| Halogen Free | IEC 60754-1; EN 50267-2-1; DIN VDE 0482-267-2-1; |  |
|  | CEI 20-37/2-1 ; BS 6425-1* |  |
| No Corrosive Gas Emission | IEC 60754-2; EN 50267-2-2; DIN VDE 0482-267-2-2; |  |
|  | CEI 20-37/2-2 ; BS 6425-2* |  |
| Minimum Smoke Emission | IEC 61034-1&2; EN 61034 -1&2; DIN VDE 0482-1034-1&2; |  |
|  | CEI 20-37/3-1&2; EN 50268-1&2*; BS 7622-1&2* |  |
| No Toxic gases | NES 02-713; NF C 20-454 |  |

Note: Asterisk * denotes superseded standard.

VOLTAGE RATING

600/1000V

36	Caledonian

Caledonian

Flame Retardant Power & Control Cables

www.caledonian-cables.co.uk	www.addison-cables.com

CABLE CONSTRUCTION

Conductor: Plain annealed copper wire, stranded according to IEC(EN) 60228 class 2. Insulation: Extruded cross-linked XLPE compound.

COLOUR CODE

Insulation Colour as per BS7671

|  | With Earth Conductor | Without Earth Conductor |
| --- | --- | --- |
| 2Cores | - | Brown, Blue |
| 3Cores | Yellow/Green, Brown, Blue | Brown, Gray, Black |
| 4Cores | Yellow/Green, Brown, Gray, Black | Brown, Gray, Black, Blue |
| 5Cores | Yellow/Green, Brown, Gray, Black, Blue | Brown, Gray, Black, Blue, Black |
| Above 5 Cores | Yellow/Green, Black Numbered | Black Numbered |

Sheath Colour: Black (other colors upon request)

Physical AND THERMAL PROPERTIES

Temperature range during operation: Max.90°C

250°C in short-circuit for 5s max. Minimum bending radius: 8 x Overall Diameter (unarmoured cable)

10 x Overall Diameter (armoured cable)

CONSTRUCTION PARAMETERS

| Conductor |  |  |  | FTX300 1Z1-R |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No. of Core X |  | No./Nominal | Nominal |  | Insulated, Non-Sheathed |  |  |
|  |  | Diameter of | Insulation |  | Nominal | Approx. |  |
| Cross Section |  |  |  |  |  |  |  |
|  |  | Strands | Thickness |  | Overall |  |  |
|  |  |  |  |  |  | Weight |  |
|  |  |  |  |  | Diameter |  |  |
| Noxmm2 |  | No./mm | mm |  | mm | kg/km |  |
| 1x1.5 |  | 7/0.53 | 0.7 |  | 3.1 | 22 |  |
| 1x2.5 |  | 7/0.67 | 0.8 |  | 3.7 | 34 |  |
| 1x4 |  | 7/0.85 | 0.8 |  | 4.3 | 50 |  |
| 1x6 |  | 7/1.04 | 0.8 |  | 4.8 | 70 |  |
| 1x10 |  | 7/1.35 | 1.0 |  | 6.2 | 116 |  |
| 1x16 |  | 7/1.70 | 1.0 |  | 7.2 | 174 |  |
| 1x25 |  | 7/2.14 | 1.2 |  | 9.0 | 276 |  |
| 1x35 |  | 7/2.52 | 1.2 |  | 10.0 | 366 |  |
| 1x50 |  | 19/1.78 | 1.4 |  | 11.9 | 502 |  |
| 1x70 |  | 19/2.14 | 1.4 |  | 13.7 | 706 |  |
| 1x95 |  | 19/2.52 | 1.6 |  | 16.0 | 974 |  |
| 1x120 |  | 37/2.03 | 1.6 |  | 17.6 | 1213 |  |
| 1x150 |  | 37/2.25 | 1.8 |  | 19.6 | 1492 |  |

ADDISON	37

ADDISON

| 1x185 | 37/2.52 | 2.0 | 21.8 | 1868 |
| --- | --- | --- | --- | --- |
| 1x240 | 61/2.25 | 2.2 | 24.4 | 2443 |
| 1x300 | 61/2.52 | 2.4 | 27.7 | 3055 |
| 1x400 | 61/2.85 | 2.6 | 31.1 | 3888 |
| 1x500 | 61/3.20 | 2.8 | 34.6 | 4880 |
| 1x630 | 127/2.52 | 2.8 | 38.6 | 6229 |

Electrical PROPERTIES

Conductor Operating Temperature : 90°C

Ambient Temperature : 30°C

Current-Carrying Capacities (Amp)

|  |  | Reference |  |  | Reference Method 12 (free |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Reference Method |  |  | Reference |  | air) |  |  |
| Conductor |  | Method 3 |  |  |  |  |  |  |
|  | 4 (enclosed |  |  | Method 11 (on a |  |  |  |  |
| cross- |  | (enclosed in | Reference Method |  |  |  |  |  |
|  | in conduit |  |  | perforated cable | Horizontal | Vertical |  |  |
| sectional | in thermally | conduit on | 1 (clipped direct) | tray, horizontal or |  |  |  |  |
| area | insulating wall etc) | a wall or in |  | vertical) | flat | flat | Trefoil |  |
|  |  | trunking etc) |  |  | spaced | spaced |  |  |

2

cables, single-phase a.c. or d.c.

|  |  |  |  |  |  |  | 2 cables, | 2 cables, |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 2 cables, | 3 or 4 2 cables, |  | 3 or 4 |  | single- |  |
|  | 2 |  | single- | cables, | single- | cables, | single- | phase |  |
| 3 or 4 | cables, | 3 or 4 |  |  |  |  | phase |  |  |
|  |  |  | phase | 3-phase | phase 3-phase |  |  | a.c. or |  |
| cables, | single- | cables, |  |  |  |  | a.c. or |  |  |
|  |  |  | a.c. or | a.c. flat | a.c. or | a.c. flat |  | d.c. |  |
| 3-phase | phase 3-phase |  |  |  |  |  | d.c. |  |  |
| a.c. | a.c. or | a.c. | d.c. flat | and | d.c. or | and | or 3 c | or 3 |  |
|  |  |  | and | touching | flat and touching |  |  | cables |  |
|  | d.c |  | touching | or trefoil touching |  | or trefoil ables three |  | three |  |
|  |  |  |  |  |  |  | phase | phase |  |

3 cables, trefoil 3-phase a.c.

| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| mm2 | A | A | A | A | A | A | A | A | A | A | A |
| 1.5 | 18 | 17 | 22 | 19 | 25 | 23 | - | - | - | - | - |
| 2.5 | 24 | 23 | 30 | 26 | 34 | 31 | - | - | - | - | - |
| 4 | 33 | 30 | 40 | 35 | 46 | 41 | - | - | - | - | - |
| 6 | 43 | 39 | 51 | 45 | 59 | 54 | - | - | - | - | - |
| 10 | 58 | 53 | 71 | 63 | 81 | 74 | - | - | - | - | - |
| 16 | 76 | 70 | 95 | 85 | 109 | 99 | - | - | - | - | - |
| 25 | 100 | 91 | 126 | 111 | 143 | 130 | 158 | 140 | 183 | 163 | 138 |
| 35 | 125 | 111 | 156 | 138 | 176 | 161 | 195 | 176 | 226 | 203 | 171 |

38	Caledonian

Caledonian

Flame Retardant Power & Control Cables

www.caledonian-cables.co.uk	www.addison-cables.com

| 50 | 149 | 135 | 189 | 168 | 228 | 209 | 293 | 215 | 274 | 246 | 209 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 70 | 189 | 170 | 240 | 214 | 293 | 268 | 308 | 279 | 351 | 318 | 270 |  |
| 95 | 228 | 205 | 290 | 259 | 355 | 326 | 375 | 341 | 426 | 389 | 330 |  |
| 120 | 263 | 235 | 336 | 299 | 413 | 379 | 436 | 398 | 495 | 453 | 385 |  |
| 150 | 300 | 270 | 375 | 328 | 476 | 436 | 505 | 461 | 570 | 524 | 445 |  |
| 185 | 341 | 306 | 426 | 370 | 545 | 500 | 579 | 530 | 651 | 600 | 511 |  |
| 240 | 400 | 358 | 500 | 433 | 644 | 590 | 686 | 630 | 769 | 711 | 606 |  |
| 300 | 459 | 410 | 573 | 493 | 743 | 681 | 794 | 730 | 886 | 824 | 701 |  |
| 400 | - | - | 684 | 584 | 868 | 793 | 915 | 849 | 1065 | 994 | 820 |  |
| 500 | - | - | 783 | 666 | 990 | 904 | 1044 | 973 | 1228 | 1150 | 936 |  |
| 630 | - | - | 900 | 764 | 1130 | 1033 | 1191 | 1115 | 1423 | 1338 | 1069 |  |

Voltage Drop (Per Amp Per Meter)

|  |  | 2 cables, single-phase a.c. |  |  |  |  |  |  |  | 3 or 4 cables, 3-phase a.c. |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Size of |  | Ref. Methods 3 |  |  | Ref. Methods 1 |  |  | Ref. Methods 3 |  |  | Ref. Methods 1, |  |  |  |  | Ref. Methods 1 |  |  |  |  |
|  | cables | and 4 (enclosed |  |  | and 11 (clipped |  |  | and 4 (enclosed |  |  |  |  |  |  |  |  |  |  |  |  |
| conductor | d.c. | in conduit etc, in |  |  | direct or on trays |  |  | in conduit etc, in |  |  | 11 and 12 (in |  |  |  |  | and 11 |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | trefoil) |  |  |  | (Flat and touching) |  |  |  |  |
|  |  | or on a wall) |  |  | touching) |  |  | or on a wall) |  |  |  |  |  |  |  |  |  |  |  |  |
| 1 | 2 |  | 3 |  | 4 |  |  |  | 5 |  |  | 6 |  |  |  | 7 |  |  |  |  |
| mm2 | mV/A/m | mV/A/m |  |  | mV/A/m |  |  | mV/A/m |  |  |  | mV/A/m |  |  |  | mV/A/m |  |  |  |  |
| 1.5 | 31 |  | 31 |  | 27 |  |  |  | 27 |  |  | 27 |  |  |  | 27 |  |  |  |  |
| 2.5 | 19 |  | 19 |  | 16 |  |  |  | 16 |  |  | 16 |  |  |  | 16 |  |  |  |  |
| 4 | 33 |  | 12 |  | 10 |  |  |  | 10 |  |  | 10 |  |  |  | 10 |  |  |  |  |
| 6 | 7.8 |  | 7.9 |  | 6.8 |  |  |  | 6.8 |  |  | 6.8 |  |  |  | 6.8 |  |  |  |  |
| 10 | 4.7 |  | 4.7 |  | 4.7 |  |  |  | 4 |  |  | 4 |  |  |  | 4 |  |  |  |  |
| 16 | 2.9 |  | 2.9 |  | 2.9 |  |  |  | 2.5 |  |  | 2.5 |  |  |  | 2.5 |  |  |  |  |
|  |  | r | x | z | r | x | z | r | x | z | r |  | x |  | z | r | x | z |  |  |
| 25 | 1.85 | 1.85 | 0.31 | 1.90 | 1.85 | 0.190 | 1.85 | 1.60 | 0.27 | 1.65 | 1.600 |  | 0.165 | 1.600 |  | 1.600 | 0.190 | 1.600 |  |  |
| 35 | 1.35 | 1.35 | 0.29 | 1.35 | 1.35 | 0.180 | 1.35 | 1.15 | 0.25 | 1.15 | 1.150 |  | 0.155 |  | 1.50 | 1.150 | 0.180 | 1.150 |  |  |
| 50 | 0.99 | 1.00 | 0.29 | 1.05 | 0.99 | 0.180 | 1.00 | 0.87 | 0.25 | 0.90 | 0.860 |  | 0.155 | 0.870 |  | 0.860 | 0.180 | 0.870 |  |  |
| 70 | 0.68 | 0.70 | 0.28 | 0.75 | 0.68 | 0.175 | 0.71 | 0.60 | 0.24 | 0.65 | 0.590 |  | 0.150 | 0.610 |  | 0.590 | 0.175 | 0.620 |  |  |
| 95 | 0.49 | 0.51 | 0.27 | 0.58 | 0.49 | 0.170 | 0.52 | 0.44 | 0.23 | 0.50 | 0.430 |  | 0.145 | 0.450 |  | 0.430 | 0.170 | 0.460 |  |  |

ADDISON	39

ADDISON

| 120 | 0.39 | 0.41 0.26 | 0.48 | 0.39 | 0.165 | 0.43 | 0.35 | 0.23 | 0.42 | 0.340 0.140 0.370 0.340 0.165 | 0.380 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 150 | 0.32 | 0.33 0.26 | 0.43 | 0.32 | 0.165 | 0.36 | 0.29 | 0.23 | 0.37 | 0.280 0.140 0.310 0.280 0.165 | 0.320 |  |
| 185 | 0.25 | 0.27 0.26 | 0.37 | 0.26 | 0.165 | 0.30 | 0.23 | 0.23 | 0.32 | 0.220 0.140 0.260 0.220 0.165 | 0.280 |  |
| 240 | 0.19 | 0.21 0.26 | 0.33 | 0.20 | 0.160 | 0.25 | 0.185 | 0.22 | 0.29 | 0.170 0.140 0.220 0.170 0.165 | 0.240 |  |
| 300 | 0.155 | 0.175 0.25 | 0.31 | 0.16 | 0.160 | 0.22 | 0.150 | 0.22 | 0.27 | 0.140 0.140 0.195 0.135 0.160 | 0.210 |  |
| 400 | 0.12 | 0.140 0.25 | 0.29 | 0.13 | 0.155 | 0.20 | 0.125 | 0.22 | 0.25 | 0.110 0.135 0.175 0.110 0.160 | 0.195 |  |
| 500 | 0.093 | 0.120 0.25 | 0.28 0.105 0.155 |  |  | 0.185 0.100 |  | 0.22 | 0.24 | 0.090 0.135 0.160 0.088 0.160 | 0.180 |  |
| 630 | 0.072 | 0.100 0.25 | 0.27 0.086 0.155 |  |  | 0.175 0.088 |  | 0.21 | 0.23 | 0.074 0.135 0.150 0.071 0.160 | 0.170 |  |
| Note : |  |  |  |  |  |  |  |  |  |  |  |  |
| r = conductor resistance at operating temperature |  |  |  |  |  |  |  |  |  |  |  |  |
| x = reactance |  |  |  |  |  |  |  |  |  |  |  |  |
| z = impedance |  |  |  |  |  |  |  |  |  |  |  |  |
| 600/1000V |  | NBS7211 |  | Flame Retardancy |  | Reduced Fire Propagation |  |  |  |  |  |  |
|  |  |  |  |  |  | NF C32-070-2.2(C1) |  |  |  |  |  |  |
|  |  |  |  | NF C32-070-2.1(C2) |  |  |  |  |  |  |  |  |
| Rated Voltage |  | Standard |  |  |  |  | IEC60332-3-24 |  |  |  |  |  |
|  |  |  | IEC60332-1-2/EN50265-2-1 |  |  |  | EN50266-2-4 |  |  |  |  |  |
|  |  |  |  |  |  | Zero |  |  |  |  |  |  |
|  |  | Low Corrosivity | Low Smoke Emission |  |  |  | Halogen Free |  |  |  |  |  |
| Low Toxicity |  | IEC60754-2 |  | IEC 61034-1&2 |  |  | IEC60754-1 |  |  |  |  |  |
|  |  | EN50267-2-2/3 |  |  |  |  |  |  |  |  |  |  |
|  |  |  | EN 50268-1&2/NF C32-073 |  |  |  | EN50267-2-1 |  |  |  |  |  |
| NES 02-713/NF C 20-454 |  | NF C 32-074 |  |  |  |  |  |  |  |  |  |  |

40	Caledonian