Caledonian

Flame Retardant Instrumentation Cables

www.caledonian-cables.co.uk	www.addison-cables.com

Flame Retardant Overall Screened Instrumentation Cables (Multicore)

RE-2X(St)H

RE-2X(St)HSWAH

APPLICATION

The LSZH versions (Part 1 Type 1&2) cables are generally use for indoor installation and suitable for wet and damp areas. Generally used within industrial process manufacturing plants for communication, data and voice transmission signals and services, Also used for the interconnection of electrical equipment and instruments, the LSZH sheath can reduce toxic smoke and fume emission.

STANDARDS

Basic design adapted to BS 5308 Part1 Type1 & 2

FIRE PERFORMANCE

| Flame Retardance (Single Vertical | EN 60332-1-2; IEC 60332-1-2; BS EN 60332-1-2; VDE |  |
| --- | --- | --- |
| Wire Test) | 0482-332-1 ; NBN C 30-004 (cat. F1); NF C32-070-2.1(C2); |  |
|  | CEI 20-35/1-2; EN 50265-2-1*; DIN VDE 0482-265-2-1* |  |
| Reduced Fire Propagation | EN 60332-3-24 (cat. C); IEC 60332-3-24; BS EN 60332-3-24; |  |
| (Vertically-mounted bundled wires | VDE 0482-332-3; NBN C 30-004 (cat. F2); NF C32-070-2.2(C1); |  |
| & cable test) | CEI 20-22/3-4; EN 50266-2-4*; DIN VDE 0482-266-2-4 |  |
| Halogen Free | IEC 60754-1; EN 50267-2-1; DIN VDE 0482-267-2-1; |  |
|  | CEI 20-37/2-1 ; BS 6425-1* |  |
| No Corrosive Gas Emission | IEC 60754-2; EN 50267-2-2; DIN VDE 0482-267-2-2; |  |
|  | CEI 20-37/2-2 ; BS 6425-2* |  |
| Minimum Smoke Emission | IEC 61034-1&2; EN 61034 -1&2; DIN VDE 0482-1034-1&2; |  |
|  | CEI 20-37/3-1&2; EN 50268-1&2*; BS 7622-1&2* |  |
| No Toxic gases | NES 02-713; NF C 20-454 |  |

Note: Asterisk * denotes superseded standard.

ADDISON	83

ADDISON

VOLTAGE RATING

300/500V

CABLE CONSTRUCTION

Conductor: Plain annealed copper wire, stranded according to IEC(EN) 60228 class 2 and 5 . Insulation: Extruded cross-linked XLPE compound.

Overall Screen: Aluminium/polyester tape with 0.5mm2 screen (7/0.3mm) tinned copper drain wire.

Inner Sheath(optional): LSZH compound Armouring(optional): Galvanised steel wire

Outer Sheath: Thermoplastic LSZH compound type LTS3 as per BS 7655-6.1 (Thermosetting LSZH compound type SW2-SW4 as per BS 7655-2.6 can be offered.). UV resistance, hydrocarbon resistance, oil resistance, anti rodent and anti termite properties can be offered as option.

COLOUR CODE

Insulation Colour: See technical information

Outer sheath: Black or blue

Physical AND THERMAL PROPERTIES

Temperature range during operation: Max.90°C for XLPE

250°C in short-circuit for 5s max. Minimum bending radius: 8 x Overall Diameter (unarmoured cable)

10 x Overall Diameter (armoured cable)

CONSTRUCTION PARAMETERS

| Conductor |  |  | RE-2X(St)H |  |  | RE-2X(St)HSWAH |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| No. of Core | No./ |  | Unarmoured |  |  | Armoured |  |  |  |
|  | Nominal | Nominal |  |  |  |  |  |  |  |
| X | Diameter | Insulation | Nominal | Approx. | Diameter | Armour | Nominal | Approx. |  |
| Cross | of | Thickness | Overall | Weight | Under | Wire | Overall | Weight |  |
| Section |  |  | Diameter |  | Armour | Diameter | Diameter |  |  |
|  | Strands |  |  |  |  |  |  |  |  |
| mm2 | No./mm | mm | mm | kg/km | mm | mm | mm | kg/km |  |
| 2x0.5 | 16/0.20 | 0.6 | 7.0 | 50 | 7.0 | 0.90 | 11.4 | 237 |  |
| 3x0.5 | 16/0.20 | 0.6 | 7.3 | 59 | 7.3 | 0.90 | 11.7 | 254 |  |
| 4x0.5 | 16/0.20 | 0.6 | 7.9 | 69 | 7.9 | 0.90 | 12.3 | 278 |  |
| 6x0.5 | 16/0.20 | 0.6 | 9.3 | 94 | 9.3 | 0.90 | 13.9 | 345 |  |
| 10x0.5 | 16/0.20 | 0.6 | 11.9 | 147 | 11.9 | 0.90 | 16.7 | 470 |  |
| 20x0.5 | 16/0.20 | 0.6 | 14.9 | 253 | 14.9 | 1.25 | 20.6 | 759 |  |
| 40x0.5 | 16/0.20 | 0.6 | 20.1 | 444 | 20.1 | 1.60 | 26.7 | 1229 |  |
| 2x0.75 | 24/0.20 | 0.6 | 7.3 | 57 | 7.3 | 0.90 | 11.7 | 251 |  |
| 3x0.75 | 24/0.20 | 0.6 | 7.7 | 68 | 7.7 | 0.90 | 12.1 | 272 |  |
| 4x0.75 | 24/0.20 | 0.6 | 8.3 | 81 | 8.3 | 0.90 | 12.9 | 310 |  |
| 6x0.75 | 24/0.20 | 0.6 | 9.9 | 114 | 9.9 | 0.90 | 14.5 | 379 |  |

84	Caledonian