Caledonian

Flame Retardant Coaxial Cables

www.caledonian-cables.co.uk	www.addison-cables.com

Flame Retardant RG59 B/U Coaxial cables

LSZH Outer Sheath

Tinned Copper Braid

Aluminium+polyester/Aluminium Tape

PE

Solid Bare Copper

LSZH Inner Sheath

Tinned Copper Drain Wire

Braid or Wire Armoured

APPLICATION

The cables are designed for CCTV, security, smoke detection and evacuation monitoring applications, where continued functionality is required during a fire situationDue. to the zero halogen low smoke construction, this cable is ideal for use in public, commercial and industrial environments.

STANDARDS

Basic design adapted to MIL-C-17

FIRE PERFORMANCE

Flame Retardance (Single Vertical EN 60332-1-2; IEC 60332-1-2; BS EN 60332-1-2; VDE Wire Test) 0482-332-1 ; NBN C 30-004 (cat. F1); NF C32-070-2.1(C2);

CEI 20-35/1-2; EN 50265-2-1*; DIN VDE 0482-265-2-1*

| Reduced Fire Propagation | EN 60332-3-24 (cat. C); IEC 60332-3-24; BS EN 60332-3-24; |  |
| --- | --- | --- |
| (Vertically-mounted bundled wires VDE 0482-332-3; NBN C 30-004 (cat. F2); NF C32-070-2.2(C1); |  |  |
| & cable test) | CEI 20-22/3-4; EN 50266-2-4*; DIN VDE 0482-266-2-4 |  |
| Halogen Free | IEC 60754-1; EN 50267-2-1; DIN VDE 0482-267-2-1; |  |
|  | CEI 20-37/2-1 ; BS 6425-1* |  |
| No Corrosive Gas Emission | IEC 60754-2; EN 50267-2-2; DIN VDE 0482-267-2-2; |  |
|  | CEI 20-37/2-2 ; BS 6425-2* |  |
| Minimum Smoke Emission | IEC 61034-1&2; EN 61034 -1&2; DIN VDE 0482-1034-1&2; |  |
|  | CEI 20-37/3-1&2; EN 50268-1&2*; BS 7622-1&2* |  |
| No Toxic gases | NES 02-713; NF C 20-454 |  |

Note: Asterisk * denotes superseded standard.

CABLE CONSTRUCTION

Conductors: Copper clad steel, solid according to IEC(EN) 60228 class 1.

Insulation: PE compound.

Overall Screen: Plain copper wire braid

Outer Sheath: Thermoplastic LSZH compound type LTS3 as per BS 7655-6.1(Thermosetting LSZH compound type SW2-SW4 as per BS 7655-2.6 can be offered.). UV resistance, hydrocarbon

ADDISON   123

ADDISON

resistance, oil resistance, anti rodent and anti termite properties can be offered as option.

Physical AND THERMAL PROPERTIES

Temperature range during operation (fixed state):-30°C - +70°C

Temperature range during installation (mobile state): -5ºC - +60ºC Minimum bending radius: 8 x Overall Diameter

Electrical Properties

| Impedance | 75±5Ω |
| --- | --- |
| Capacitance | 67 nF/km |
| Velocity ratio(%) | 66 |
| Insulation resistance | >2000 Mohm.Km |
| Shield coverage | 95% |
| DC resistance |  |
| Inner conductor | 158 Ω/km |
| Outer conductor | 9.0 Ω/km |

Attenuation

| Frequency(MHz) | Attenuation (dB/100 m) | Attenuation (dB/100ft) |
| --- | --- | --- |
| 50 | 7.4 | 2.26 |
| 100 | 10.7 | 3.26 |
| 200 | 15.7 | 4.79 |
| 400 | 22.7 | 6.92 |
| 500 | 25.7 | 7.84 |
| 600 | 28.7 | 8.75 |
| 860 | 34.8 | 10.61 |
| 1000 | 38.0 | 11.59 |

Return Loss

| Frequency(MHz) | Return Loss (dB) |
| --- | --- |
| 30-300 MHz | >31dB |
| 300-600 MHz | >28dB |
| 600-900 MHz | >24dB |

124	Caledonian

Caledonian

Flame Retardant Coaxial Cables

www.caledonian-cables.co.uk	www.addison-cables.com

CONSTRUCTION PARAMETERS

| Cable | Conductor |  | Nominal |  |  | Nominal | Nominal | Approx. |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Insulation |  |  | Screen | Overall |  |  |
| Code | Diameter |  |  |  |  |  |  | Weight |  |
|  |  |  | Diameter |  |  | No.x Diameter | Diameter |  |  |
|  | mm |  | mm |  |  | No. x mm | mm | kg/km |  |
| FTX-RG59 B/U | 0.58 ± 0.03 3.70 ± 0.10 m |  |  |  |  | 120 x 0.15 | 6.20 | 60.3 |  |
| 300/500V | NMIL-C-17 |  | Flame Retardancy | Reduced Fire Propagation |  |  |  |  |  |
|  |  |  |  |  | NF C32-070-2.2(C1) |  |  |  |  |
| Rated Voltage |  |  | NF C32-070-2.1(C2) |  | IEC60332-3-24 |  |  |  |  |
|  | Standard | IEC60332-1-2/EN50265-2-1 |  |  |  | EN50266-2-4 |  |  |  |
|  |  |  |  |  | Zero |  |  |  |  |
|  | Low Corrosivity |  | Low Smoke Emission |  |  | Halogen Free |  |  |  |
|  | IEC60754-2 |  |  |  |  |  |  |  |  |
| Low Toxicity |  |  | IEC 61034-1&2 |  |  | IEC60754-1 |  |  |  |
|  | EN50267-2-2/3 |  |  |  |  |  |  |  |  |
| NES 02-713/NF C 20-454 | NF C 32-074 | EN 50268-1&2/NF C32-073 |  |  |  | EN50267-2-1 |  |  |  |

ADDISON   125