Caledonian

Flame Retardant Power & Control Cables

www.caledonian-cables.co.uk	www.addison-cables.com

600/1000V XLPE Insulated, LSZH Sheathed, Armoured Power Cables (Single Core)

FTX300 1RZ1-R (CU/XLPE/LSZH 600/1000V Class 2)

FTX300 1RZ1MZ1-R (CU/XLPE/LSZH/AWA/LSZH 600/1000V Class 2)

APPLICATION

The cables is mainly used in power stations, mass transit underground passenger systems, airports, petrochemical plants, hotels, hospitals, and high-rise buildings.

STANDARDS

Basic design adapted to IEC 60502-1; BS 6724; BS 7211

FIRE PERFORMANCE

| Flame Retardance (Single Vertical | EN 60332-1-2; IEC 60332-1-2; BS EN 60332-1-2; VDE |  |
| --- | --- | --- |
|  | 0482-332-1 ; NBN C 30-004 (cat. F1); NF C32-070-2.1(C2); |  |
| Wire Test) | CEI 20-35/1-2; EN 50265-2-1*; DIN VDE 0482-265-2-1* |  |
| Reduced Fire Propagation | EN 60332-3-24 (cat. C); IEC 60332-3-24; BS EN 60332-3-24; |  |
| (Vertically-mounted bundled wires | VDE 0482-332-3; NBN C 30-004 (cat. F2); NF C32-070-2.2(C1); |  |
| & cable test) | CEI 20-22/3-4; EN 50266-2-4*; DIN VDE 0482-266-2-4 |  |
| Halogen Free | IEC 60754-1; EN 50267-2-1; DIN VDE 0482-267-2-1; |  |
|  | CEI 20-37/2-1 ; BS 6425-1* |  |
| No Corrosive Gas Emission | IEC 60754-2; EN 50267-2-2; DIN VDE 0482-267-2-2; |  |
|  | CEI 20-37/2-2 ; BS 6425-2* |  |
| Minimum Smoke Emission | IEC 61034-1&2; EN 61034 -1&2; DIN VDE 0482-1034-1&2; |  |
|  | CEI 20-37/3-1&2; EN 50268-1&2*; BS 7622-1&2* |  |
| No Toxic gases | NES 02-713; NF C 20-454 |  |

Note: Asterisk * denotes superseded standard.

VOLTAGE RATING

600/1000V

ADDISON	41

ADDISON

CABLE CONSTRUCTION

Conductor: Plain annealed copper wire, stranded according to IEC(EN) 60228 class 2. Insulation: Extruded cross-linked XLPE compound.

Inner sheath(optional): LSZH Compound Armouring(optional): Aluminium Wire

Outer Sheath: Thermoplastic LSZH compound type LTS3 as per BS 7655-6.1 (Thermosetting LSZH compound type SW2-SW4 as per BS 7655-2.6 can be offered.). UV resistance, hydrocarbon resistance, oil resistance, anti rodent and anti termite properties can be offered as option.

COLOUR CODE

Insulation Colour as per BS7671

|  | With Earth Conductor | Without Earth Conductor |
| --- | --- | --- |
| 2Cores | - | Brown, Blue |
| 3Cores | Yellow/Green, Brown, Blue | Brown, Gray, Black |
| 4Cores | Yellow/Green, Brown, Gray, Black | Brown, Gray, Black, Blue |
| 5Cores | Yellow/Green, Brown, Gray, Black, Blue | Brown, Gray, Black, Blue, Black |
| Above 5 Cores | Yellow/Green, Black Numbered | Black Numbered |

Sheath Colour: Black (other colors upon request)

Physical AND THERMAL PROPERTIES

Temperature range during operation: Max.90°C

250°C in short-circuit for 5s max. Minimum bending radius: 8 x Overall Diameter (unarmoured cable)

10 x Overall Diameter (armoured cable)

CONSTRUCTION PARAMETERS

|  | Conductor |  | FTX300 1RZ1-R |  |  |  | FTX300 1RZ1MZ1-R |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | No. of | No./ |  | Unarmoured |  |  | Armoured |  |  |  |
|  |  | Nominal | Nominal |  |  |  |  |  |  |  |
|  | Core X |  |  |  |  |  |  |  |  |  |
|  |  | Diameter | Insulation | Nominal | Approx. | Diameter | Armour | Nominal | Approx. |  |
|  | Cross |  |  |  |  |  |  |  |  |  |
|  |  | of | Thickness | Overall |  | Under | Wire | Overall |  |  |
|  | Section |  |  |  | Weight |  |  |  | Weight |  |
|  |  | Strands |  | Diameter |  | Armour | Diameter | Diameter |  |  |
|  | mm2 | No./mm | mm | mm | kg/km | mm | mm | mm | kg/km |  |
|  | 1x1.5 | 7/0.53 | 0.7 | 6 | 48 | — | — | — | — |  |
|  | 1x2.5 | 7/0.67 | 0.7 | 6.4 | 63 | — | — | — | — |  |
|  | 1x4 | 7/0.85 | 0.7 | 7.0 | 78 | — | — | — | — |  |
|  | 1x6 | 7/1.04 | 0.7 | 7.5 | 105 | — | — | — | — |  |
|  | 1x10 | 7/1.35 | 0.7 | 8.5 | 151 | — | — | — | — |  |
|  | 1x16 | 7/1.70 | 0.7 | 9.5 | 211 | — | — | — | — |  |
|  | 1x25 | 7/2.14 | 0.9 | 11.2 | 315 | — | — | — | — |  |
|  | 1x35 | 7/2.52 | 0.9 | 12.4 | 416 | — | — | — | — |  |
|  | 1x50 | 19/1.78 | 1.0 | 14 | 569 | — | — | — | — |  |
| 42 | Caledonian |  |  |  |  |  |  |  |  |  |

Caledonian

Flame Retardant Power & Control Cables

www.caledonian-cables.co.uk	www.addison-cables.com

| 1x70 | 19/2.14 | 1.1 | 16 | 792 | 15.4 | 1.25 | 21.5 | 960 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1x95 | 19/2.52 | 1.1 | 18 | 1068 | 17.3 | 1.25 | 23.4 | 1240 |
| 1x120 | 37/2.03 | 1.2 | 20 | 1325 | 19.1 | 1.6 | 25.9 | 1650 |
| 1x150 | 37/2.25 | 1.4 | 22 | 1627 | 21.1 | 1.6 | 27.9 | 1970 |
| 1x185 | 37/2.52 | 1.6 | 24.4 | 2021 | 23.2 | 1.6 | 30.1 | 2390 |
| 1x240 | 61/2.25 | 1.7 | 27.5 | 2617 | 26.2 | 1.6 | 33.2 | 3040 |
| 1x300 | 61/2.52 | 1.8 | 30.3 | 3252 | 28.8 | 1.6 | 35.8 | 3790 |
| 1x400 | 61/2.85 | 2.0 | 33.9 | 4131 | 32.7 | 2.0 | 40.9 | 4790 |
| 1x500 | 61/3.20 | 2.2 | 37.6 | 5175 | 36.2 | 2.0 | 44.6 | 5880 |
| 1x630 | 127/2.52 | 2.4 | 42.4 | 6631 | 40.6 | 2.0 | 49.2 | 7400 |
| 1x800 | 127/2.85 | 2.6 | 47.3 | 8412 | 45.7 | 2.5 | 55.7 | 9500 |
| 1x1000 | 127/3.20 | 2.8 | 52.4 | 10530 | 50.6 | 2.5 | 61.0 | 11750 |

Electrical PROPERTIES

Conductor Operating Temperature : 90°C

Ambient Temperature : 30°C

FTX300 1RZ1-R

Current-Carrying Capacities (Amp)

|  | Reference |  | Reference |  |  |  |  |  | Reference Method 12 (free |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Method 4 |  |  |  |  |  | Reference |  |  | air) |  |  |
| Conductor |  |  | Method 3 |  |  |  |  |  |  |  |  |  |
|  | (enclosed |  |  |  |  |  | Method 11 (on a |  |  |  |  |  |
| cross- |  |  | (enclosed in |  | Reference Method |  |  |  |  |  |  |  |
| sectional | in conduit |  | conduit on a wall |  | 1 (clipped direct) |  | perforated cable |  | Horizontal | Vertical |  |  |
| area | in thermally |  | or in trunking |  |  |  | tray, horizontal or |  | flat | flat | Trefoil |  |
|  | insulating wall |  |  |  |  |  | vertical) |  | spaced | spaced |  |  |
|  |  |  | etc) |  |  |  |  |  |  |  |  |  |
|  | etc) |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | 2 cables, | 2 |  |  |
|  |  |  |  |  |  |  |  |  |  | cables, |  |  |
|  | 2 |  | 2 |  | 2 cables, | 3 or 4 | 2 cables, | 3 or 4 | single- | single- |  |  |
|  |  |  |  |  | single- | cables, | single- | cables, | phase |  |  |  |
|  | cables, | 3 or 4 | cables, | 3 or 4 |  |  |  |  |  | phase | 3 cables, |  |
|  |  |  |  |  | phase | 3-phase | phase | 3-phase | a.c. or |  |  |  |
|  | single- | cables, | single- | cables, |  |  |  |  |  | a.c. or | trefoil |  |
|  | phase | 3-phase | phase | 3-phase | a.c. or | a.c. flat | a.c. or | a.c. flat | d.c. | d.c. | 3-phase |  |
|  | a.c. or | a.c. | a.c. or | a.c. | d.c. flat | and | d.c. or | and | or 3 c | or 3 | a.c. |  |
|  | d.c. |  | d.c |  | and | touching | flat and | touching | ables | cables |  |  |
|  |  |  |  |  | touching | or trefoil | touching | or trefoil | three |  |  |  |
|  |  |  |  |  |  |  |  |  |  | three |  |  |
|  |  |  |  |  |  |  |  |  | phase |  |  |  |
|  |  |  |  |  |  |  |  |  |  | phase |  |  |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 |  |
| mm2 | A | A | A | A | A | A | A | A | A | A | A |  |
| 1.5 | 18 | 17 | 22 | 19 | 25 | 23 | - | - | - | - | - |  |
| 2.5 | 24 | 23 | 30 | 26 | 34 | 31 | - | - | - | - | - |  |
| 4 | 33 | 30 | 40 | 35 | 46 | 41 | - | - | - | - | - |  |
| 6 | 43 | 39 | 51 | 45 | 59 | 54 | - | - | - | - | - |  |

ADDISON	43

ADDISON

| 10 | 58 | 53 | 71 | 63 | 81 | 74 | - | - | - | - | - |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 16 | 76 | 70 | 95 | 85 | 109 | 99 | - | - | - | - | - |
| 25 | 100 | 91 | 126 | 111 | 143 | 130 | 158 | 140 | 183 | 163 | 138 |
| 35 | 125 | 111 | 156 | 138 | 176 | 161 | 195 | 176 | 226 | 203 | 171 |
| 50 | 149 | 135 | 189 | 168 | 228 | 209 | 293 | 215 | 274 | 246 | 209 |
| 70 | 189 | 170 | 240 | 214 | 293 | 268 | 308 | 279 | 351 | 318 | 270 |
| 95 | 228 | 205 | 290 | 259 | 355 | 326 | 375 | 341 | 426 | 389 | 330 |
| 120 | 263 | 235 | 336 | 299 | 413 | 379 | 436 | 398 | 495 | 453 | 385 |
| 150 | 300 | 270 | 375 | 328 | 476 | 436 | 505 | 461 | 570 | 524 | 445 |
| 185 | 341 | 306 | 426 | 370 | 545 | 500 | 579 | 530 | 651 | 600 | 511 |
| 240 | 400 | 358 | 500 | 433 | 644 | 590 | 686 | 630 | 769 | 711 | 606 |
| 300 | 459 | 410 | 573 | 493 | 743 | 681 | 794 | 730 | 886 | 824 | 701 |
| 400 | - | - | 684 | 584 | 868 | 793 | 915 | 849 | 1065 | 994 | 820 |
| 500 | - | - | 783 | 666 | 990 | 904 | 1044 | 973 | 1228 | 1150 | 936 |
| 630 | - | - | 900 | 764 | 1130 | 1033 | 1191 | 1115 | 1423 | 1338 | 1069 |
| 800 | - | - | - | - | 1288 | 1179 | 1358 | 1275 | 1580 | 1485 | 1214 |
| 1000 | - | - | - | - | 1443 | 1323 | 1520 | 1436 | 1775 | 1671 | 1349 |

Voltage Drop (Per Amp Per Meter)

Size of conductor

|  | 2 cables, single-phase a.c. |  | 3 or 4 cables, 3-phase a.c. |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 2 | Ref. Methods 3 | Ref. Methods 1 | Ref. Methods 3 | Ref. Methods 1, | Ref. Methods 1 |  |
| cables | and 4 (enclosed | and 11 (clipped | and 4 (enclosed |  |  |  |
| d.c. | in conduit etc, in | direct or on trays | in conduit etc, in | 11 and 12 (in | and 11 |  |
|  |  |  |  | trefoil) | (Flat and touching) |  |
|  | or on a wall) | touching) | or on a wall) |  |  |  |

| 1 | 2 |  | 3 |  | 4 |  |  |  | 5 |  |  | 6 |  |  | 7 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| mm2 | mV/A/m | mV/A/m |  |  | mV/A/m |  |  | mV/A/m |  |  | mV/A/m |  |  | mV/A/m |  |  |
| 1.5 | 31 |  | 31 |  | 27 |  |  |  | 27 |  |  | 27 |  |  | 27 |  |
| 2.5 | 19 |  | 19 |  | 16 |  |  |  | 16 |  |  | 16 |  |  | 16 |  |
| 4 | 33 |  | 12 |  | 10 |  |  |  | 10 |  |  | 10 |  |  | 10 |  |
| 6 | 7.8 |  | 7.9 |  | 6.8 |  |  |  | 6.8 |  |  | 6.8 |  |  | 6.8 |  |
| 10 | 4.7 |  | 4.7 |  | 4.7 |  |  |  | 4 |  |  | 4 |  |  | 4 |  |
| 16 | 2.9 |  | 2.9 |  | 2.9 |  |  |  | 2.5 |  |  | 2.5 |  |  | 2.5 |  |
|  |  | r | x | z | r | x | z | r | x | z | r | x | z | r | x | z |
| 25 | 1.85 | 1.85 | 0.31 | 1.90 | 1.85 | 0.190 | 1.85 | 1.60 | 0.27 | 1.65 | 1.600 | 0.165 | 1.600 | 1.600 | 0.190 | 1.600 |
| 35 | 1.35 | 1.35 | 0.29 | 1.35 | 1.35 | 0.180 | 1.35 | 1.15 | 0.25 | 1.15 | 1.150 | 0.155 | 1.50 | 1.150 | 0.180 | 1.150 |
| 50 | 0.99 | 1.00 | 0.29 | 1.05 | 0.99 | 0.180 | 1.00 | 0.87 | 0.25 | 0.90 | 0.860 | 0.155 | 0.870 | 0.860 | 0.180 | 0.870 |
| 70 | 0.68 | 0.70 | 0.28 | 0.75 | 0.68 | 0.175 | 0.71 | 0.60 | 0.24 | 0.65 | 0.590 | 0.150 | 0.610 | 0.590 | 0.175 | 0.620 |
| 95 | 0.49 | 0.51 | 0.27 | 0.58 | 0.49 | 0.170 | 0.52 | 0.44 | 0.23 | 0.50 | 0.430 | 0.145 | 0.450 | 0.430 | 0.170 | 0.460 |
| 120 | 0.39 | 0.41 | 0.26 | 0.48 | 0.39 | 0.165 | 0.43 | 0.35 | 0.23 | 0.42 | 0.340 | 0.140 | 0.370 | 0.340 | 0.165 | 0.380 |

44	Caledonian

Caledonian

Flame Retardant Power & Control Cables

www.caledonian-cables.co.uk	www.addison-cables.com

| 150 | 0.32 | 0.33 | 0.26 | 0.43 | 0.32 | 0.165 | 0.36 | 0.29 | 0.23 | 0.37 | 0.280 | 0.140 | 0.310 | 0.280 | 0.165 | 0.320 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 185 | 0.25 | 0.27 | 0.26 | 0.37 | 0.26 | 0.165 | 0.30 | 0.23 | 0.23 | 0.32 | 0.220 | 0.140 | 0.260 | 0.220 | 0.165 | 0.280 |
| 240 | 0.19 | 0.21 | 0.26 | 0.33 | 0.20 | 0.160 | 0.25 | 0.185 | 0.22 | 0.29 | 0.170 | 0.140 | 0.220 | 0.170 | 0.165 | 0.240 |
| 300 | 0.155 | 0.175 | 0.25 | 0.31 | 0.16 | 0.160 | 0.22 | 0.150 | 0.22 | 0.27 | 0.140 | 0.140 | 0.195 | 0.135 | 0.160 | 0.210 |
| 400 | 0.12 | 0.140 | 0.25 | 0.29 | 0.13 | 0.155 | 0.20 | 0.125 | 0.22 | 0.25 | 0.110 | 0.135 | 0.175 | 0.110 | 0.160 | 0.195 |
| 500 | 0.093 | 0.120 | 0.25 | 0.28 | 0.105 | 0.155 | 0.185 | 0.100 | 0.22 | 0.24 | 0.090 | 0.135 | 0.160 | 0.088 | 0.160 | 0.180 |
| 630 | 0.072 | 0.100 | 0.25 | 0.27 | 0.086 | 0.155 | 0.175 | 0.088 | 0.21 | 0.23 | 0.074 | 0.135 | 0.150 | 0.071 | 0.160 | 0.170 |
| 800 | 0.056 | - | - | - | 0.072 | 0.150 | 0.170 | - | - | - | 0.062 | 0.130 | 0.145 | 0.059 | 0.155 | 0.165 |
| 1000 | 0.045 | - | - | - | 0.063 | 0.150 | 0.165 | - | - | - | 0.055 | 0.130 | 0.140 | 0.050 | 0.155 | 0.165 |

FTX300 1RZ1MZ1-R

Current-Carrying Capacities (Amp)

| Conductor | Reference Method |  | Reference Method |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 11 (on a perforated |  | Reference |  |  |  |  |  |
| cross- | 1 (clipped |  |  |  |  |  |  |  |  |  |
|  |  |  | horizontal cable tray or |  | Method 12 | In single-way ducts |  | Laid direct in ground |  |  |
| sectional | direct) |  |  |  |  |  |  |  |  |  |
|  |  |  | Reference Method 13 |  | (free air) |  |  |  |  |  |
| area |  |  |  |  |  |  |  |  |  |  |
|  |  |  | [free air] ) |  |  |  |  |  |  |  |
|  | 2 |  | 2 |  |  | 2 |  | 2 |  |  |
|  | cables, | 3 or 4 | cables, | 3 or 4 | 3 cables | cables, | 3 or 4 | cables, | 3 or 4 |  |
|  | single- | cables, | single- | cables, | 3-phase | single- | cables, | single- | cables, |  |
|  | phase | 3-phase | phase | 3-phase | a.c. trefoil | phase | 3-phase | phase | 3-phase |  |
|  | a.c. or | a.c. | a.c. or | a.c. | touching | a.c. or | a.c. | a.c. or | a.c. |  |
|  | d.c. |  | d.c. |  |  | d.c. |  | d.c. |  |  |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 |  |
| mm2 | A | A | A | A | A | A | A | A | A |  |
| 70 | 303 | 277 | 322 | 293 | 285 | 310 | 280 | 340 | 290 |  |
| 95 | 367 | 333 | 389 | 352 | 346 | 365 | 330 | 405 | 345 |  |
| 120 | 425 | 383 | 449 | 405 | 402 | 410 | 370 | 460 | 389 |  |
| 150 | 488 | 437 | 516 | 462 | 463 | 445 | 405 | 510 | 435 |  |
| 185 | 557 | 496 | 587 | 524 | 529 | 485 | 440 | 580 | 490 |  |
| 240 | 656 | 579 | 689 | 612 | 625 | 550 | 500 | 670 | 560 |  |
| 300 | 755 | 662 | 792 | 700 | 720 | 610 | 550 | 750 | 630 |  |
| 400 | 853 | 717 | 899 | 767 | 815 | 640 | 580 | 830 | 700 |  |
| 500 | 962 | 791 | 1016 | 851 | 918 | 690 | 620 | 910 | 770 |  |
| 630 | 1082 | 861 | 1146 | 935 | 1027 | 750 | 670 | 1000 | 840 |  |
| 800 | 1170 | 904 | 1246 | 987 | 1119 | 828 | 735 | 1117 | 931 |  |
| 1000 | 1261 | 961 | 1345 | 1055 | 1214 | 919 | 811 | 1254 | 1038 |  |

ADDISON	45

ADDISON

Voltage Drop (Per Amp Per Meter)

|  |  | 2 cables single- |  |  |  |  |  |  |  |  |  |  |  |  | 2 cables |  |  | 3 or 4 cables, |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  | 3 or 4 cables three-phase a.c. |  |  |  |  |  |  |  | singlephase |  |  | 3-phase a.c. |  |  |
| Conductor |  | phase a.c. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 2 cables |  |  |  |  |  |  |  |  |  |  |  |  |  |  | a.c. |  | touching |  |  |
| cross- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | Reference Method 1, |  |  |  |  |  |  |  |  |  |  |  |  |  |
| sectional | d.c. | Reference Method 1 |  |  |  |  |  |  |  | Reference Method |  |  |  |  | In |  | In | In | In |  |
| area |  |  | & |  |  |  | 11 |  |  |  | 1 & 11 |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | & 12 (in trefoil |  |  |  |  |  |  |  | ducts |  | ground | ducts | ground |  |
|  |  | 11 (touching) |  |  |  |  |  |  |  | (Flat touching) |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | touching) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1 | 2 |  | 3 |  |  |  | 4 |  |  |  | 5 |  |  |  | 6 |  | 7 | 8 | 9 |  |
| mm2 | mV/A/m |  | mV/A/m |  |  |  | mV/A/m |  |  | mV/A/m |  |  |  |  | mV/A/m |  | mV/A/m | mV/A/m | mV/A/m |  |
|  |  | r |  | x |  | z | r | x | z | r |  | x |  | z |  |  |  |  |  |  |
| 70 | 0.67 | 0.68 |  | 0.20 |  | 0.71 | 0.59 | 0.17 | 0.62 | 0.6 |  | 0.25 |  | 0.65 | 0.80 |  | 0.70 | 0.70 | 0.61 |  |
| 95 | 0.49 | 0.51 |  | 0.195 |  | 0.55 | 0.44 | 0.17 | 0.47 | 0.46 |  | 0.24 |  | 0.52 | 0.65 |  | 0.53 | 0.56 | 0.46 |  |
| 120 | 0.39 | 0.41 |  | 0.190 |  | 0.45 | 0.35 | 0.165 | 0.39 | 0.38 |  | 0.24 |  | 0.44 | 0.55 |  | 0.43 | 0.48 | 0.37 |  |
| 150 | 0.31 | 0.33 |  | 0.185 |  | 0.38 | 0.29 | 0.160 | 0.33 | 0.31 |  | 0.23 |  | 0.39 | 0.50 |  | 0.37 | 0.43 | 0.32 |  |
| 185 | 0.25 | 0.27 |  | 0.185 |  | 0.33 | 0.23 | 0.160 | 0.28 | 0.26 |  | 0.23 |  | 0.34 | 0.45 |  | 0.31 | 0.39 | 0.27 |  |
| 240 | 0.195 | 0.21 |  | 0.180 |  | 0.28 | 0.18 | 0.155 | 0.24 | 0.21 |  | 0.22 |  | 0.30 | 0.40 |  | 0.26 | 0.35 | 0.23 |  |
| 300 | 0.155 | 0.17 |  | 0.175 |  | 0.25 | 0.145 | 0.150 | 0.21 | 0.17 |  | 0.22 |  | 0.28 | 0.37 |  | 0.24 | 0.32 | 0.21 |  |
| 400 | 0.115 | 0.145 |  | 0.170 |  | 0.22 | 0.125 | 0.150 | 0.195 | 0.160 |  | 0.21 |  | 0.27 | 0.35 |  | 0.21 | 0.30 | 0.19 |  |
| 500 | 0.093 | 0.125 |  | 0.170 |  | 0.21 | 0.105 | 0.145 | 0.180 | 0.145 |  | 0.20 |  | 0.25 | 0.33 |  | 0.20 | 0.28 | 0.18 |  |
| 630 | 0.073 | 0.105 |  | 0.165 |  | 0.195 | 0.092 | 0.145 | 0.170 | 0.135 |  | 0.195 |  | 0.24 | 0.30 |  | 0.19 | 0.26 | 0.17 |  |
| 800 | 0.056 | 0.090 |  | 0.160 |  | 0.190 | 0.086 | 0.140 | 0.165 | 0.130 |  | 0.180 |  | 0.23 | 0.28 |  | 0.18 | 0.24 | 0.16 |  |
| 1000 | 0.045 | 0.092 |  | 0.155 |  | 0.180 | 0.080 | 0.135 | 0.155 | 0.125 |  | 0.170 |  | 0.21 | 0.26 |  | 0.17 | 0.22 | 0.15 |  |

Note :

r = conductor resistance at operating temperature x = reactance

z = impedance

| 600/1000V | IECN60502-1 | NBS7211 | NBS6724 | Flame Retardancy |  |
| --- | --- | --- | --- | --- | --- |
| Rated Voltage | Standard | Standard | Standard | NF C32-070-2.1(C2) |  |
|  |  |  |  | IEC60332-1-2/EN50265-2-1 |  |
|  |  |  |  | Zero |  |
|  | Low Corrosivity | Low Smoke Emission | Reduced Fire Propagation | Halogen Free |  |
| Low Toxicity | IEC60754-2 | IEC 61034-1&2 | NF C32-070-2.2(C1) | IEC60754-1 |  |
|  | EN50267-2-2/3 |  |  |  |  |
|  |  | EN 50268-1&2/NF C32-073 | IEC60332-3-24/EN50266-2-4 | EN50267-2-1 |  |
| NES 02-713/NF C 20-454 | NF C 32-074 |  |  |  |  |

46	Caledonian