Caledonian

Flame Retardant Power & Control Cables

www.caledonian-cables.co.uk	www.addison-cables.com

300/500V XLPE Insulated, LSZH Sheathed, Screened Power Cables (Multicore)

FTX200 05ROZ1-R (CU/XLPE/OSCR/LSZH 300/500V Class 2)

APPLICATION

The cables is mainly used in power stations, mass transit underground passenger systems, airports, petrochemical plants, hotels, hospitals, and high-rise buildings.

STANDARDS

Basic design adapted to BS 5308

FIRE PERFORMANCE

Flame Retardance (Single Vertical EN 60332-1-2; IEC 60332-1-2; BS EN 60332-1-2; VDE Wire Test) 0482-332-1 ; NBN C 30-004 (cat. F1); NF C32-070-2.1(C2);

CEI 20-35/1-2; EN 50265-2-1*; DIN VDE 0482-265-2-1*

| Reduced Fire Propagation | EN 60332-3-24 (cat. C); IEC 60332-3-24; BS EN 60332-3-24; |  |
| --- | --- | --- |
| (Vertically-mounted bundled wires VDE 0482-332-3; NBN C 30-004 (cat. F2); NF C32-070-2.2(C1); |  |  |
| & cable test) | CEI 20-22/3-4; EN 50266-2-4*; DIN VDE 0482-266-2-4 |  |
| Halogen Free | IEC 60754-1; EN 50267-2-1; DIN VDE 0482-267-2-1; |  |
|  | CEI 20-37/2-1 ; BS 6425-1* |  |
| No Corrosive Gas Emission | IEC 60754-2; EN 50267-2-2; DIN VDE 0482-267-2-2; |  |
|  | CEI 20-37/2-2 ; BS 6425-2* |  |
| Minimum Smoke Emission | IEC 61034-1&2; EN 61034 -1&2; DIN VDE 0482-1034-1&2; |  |
|  | CEI 20-37/3-1&2; EN 50268-1&2*; BS 7622-1&2* |  |
| No Toxic gases | NES 02-713; NF C 20-454 |  |

Note: Asterisk * denotes superseded standard.

VOLTAGE RATING

300/500V

CABLE CONSTRUCTION

Conductor: Plain annealed copper wire, stranded according to IEC(EN) 60228 class 2.

ADDISON	15

ADDISON

Insulation: Extruded cross-linked XLPE compound.

Filler, binder(if any): PP, Mylar tape

Circuit Protective Conductor: Annealed plain copper (class 2)

Overall Screen: Aluminium/polyester tape

Outer Sheath: Thermoplastic LSZH compound type LTS3 as per BS 7655-6.1 (Thermosetting LSZH compound type SW2-SW4 as per BS 7655-2.6 can be offered.). UV resistance, hydrocarbon resistance, oil resistance, anti rodent and anti termite properties can be offered as option.

COLOUR CODE

Insulation Colour as per BS7671

|  | With Earth Conductor | Without Earth Conductor |
| --- | --- | --- |
| 2Cores | - | Brown, Blue |
| 3Cores | Yellow/Green, Brown, Blue | Brown, Gray, Black |
| 4Cores | Yellow/Green, Brown, Gray, Black | Brown, Gray, Black, Blue |
| 5Cores | Yellow/Green, Brown, Gray, Black, Blue | Brown, Gray, Black, Blue, Black |
| Above 5 Cores | Yellow/Green, Black Numbered | Black Numbered |

Sheath Colour: Black (other colors upon request)

Physical AND THERMAL PROPERTIES

Temperature range during operation: Max.90°C for XLPE

250°C in short-circuit for 5s max.

Minimum bending radius: 6 x Overall Diameter

CONSTRUCTION PARAMETERS

|  | Conductor |  |  |  | Ftx200 05roz1-R |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | No./ |  |  | Cross- |  |  | Max.Dc |  |  |
| No. Of |  | Nominal |  | Section |  |  |  |  |  |
|  | Nominal |  | Nominal |  | Nominal | Nominal | Resistance |  |  |
| Core X |  | Overall |  | Area Of |  |  |  | Approx. |  |
|  | Diameter |  | Insulation |  | Sheath | Overall | Of |  |  |
| Cross | Of | Diameter | Thickness | Circuit | Thickness | Diameter | Conductor | Weight |  |
| Section | Strands | Conductor |  | Protective |  |  | @20°C |  |  |
|  |  |  |  | Conductor |  |  |  |  |  |
| Noxmm2 | No./mm | mm | mm | mm2 | mm | mm | Ω/km | Kg/km |  |
| 7x1.0 | 7i0.44 | 1.32 | 0.6 | 1.0 | 1.0 | 11.2 | 18.1 | 186 |  |
| 7x1.5 | 7i0.53 | 1.59 | 0.7 | 1.5 | 1.1 | 12.9 | 12.1 | 253 |  |
| 7x2.5 | 7i0.67 | 2.01 | 0.8 | 2.5 | 1.2 | 14.9 | 7.41 | 365 |  |
| 12x1.5 | 7i0.53 | 1.59 | 0.7 | 1.5 | 1.2 | 16.8 | 12.1 | 404 |  |
| 12x2.5 | 7i0.67 | 2.01 | 0.8 | 2.5 | 1.4 | 19.8 | 7.41 | 595 |  |
| 19x1.5 | 7i0.53 | 1.59 | 0.7 | 1.5 | 1.3 | 19.7 | 12.1 | 600 |  |
| 19x2.5 | 7i0.67 | 2.01 | 0.8 | 2.5 | 1.5 | 23.2 | 7.41 | 885 |  |

Electrical PROPERTIES

Conductor Operating Temperature : 90°C

Ambient Temperature : 30°C

16	Caledonian

Caledonian

Flame Retardant Power & Control Cables

www.caledonian-cables.co.uk	www.addison-cables.com

Current-Carrying Capacities (Amp)

|  |  |  | Reference |  |  |  | Reference |  | Reference Method 12 (free |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Conductor | Reference Method |  | Method 3 |  |  |  |  |  |  | air) |  |  |
|  |  |  |  |  |  |  | Method 11 (on a |  |  |  |  |  |
| cross- | 4 (enclosed in |  | (enclosed in |  | Reference Method |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | perforated cable |  | Horizontal | Vertical |  |  |
| sectional | conduit in thermally |  | conduit on |  | 1 (clipped direct) |  | tray, horizontal or |  | flat | flat | Trefoil |  |
| area | insulating wall etc) |  | a wall or in |  |  |  | vertical) |  | spaced | spaced |  |  |
|  |  |  | trunking etc) |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | 2 cables, | 2 |  |  |
|  |  |  |  |  |  |  |  |  |  | cables, |  |  |
|  | 2 |  | 2 |  | 2 cables, | 3 or 4 | 2 cables, | 3 or 4 | single- | single- | 3 |  |
|  |  |  |  |  | single- | cables, | single- | cables, | phase |  |  |  |
|  | cables, | 3 or 4 | cables, | 3 or 4 |  |  |  |  |  | phase | cables, |  |
|  |  |  |  |  | phase | 3-phase | phase | 3-phase | a.c. or |  |  |  |
|  | single- | cables, | single- | cables, |  |  |  |  |  | a.c. or | trefoil |  |
|  | phase | 3-phase | phase | 3-phase | a.c. or | a.c. flat | a.c. or | a.c. flat | d.c. | d.c. | 3- |  |
|  | a.c. or | a.c. | a.c. or | a.c. | d.c. flat | and | d.c. or | and | or 3 c | or 3 | phase |  |
|  | d.c. |  | d.c |  | and | touching | flat and | touching | ables | cables | a.c. |  |
|  |  |  |  |  | touching | or trefoil | touching | or trefoil | three |  |  |  |
|  |  |  |  |  |  |  |  |  |  | three |  |  |
|  |  |  |  |  |  |  |  |  | phase |  |  |  |
|  |  |  |  |  |  |  |  |  |  | phase |  |  |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 |  |
| mm2 | A | A | A | A | A | A | A | A | A | A | A |  |
| 1.5 | 18 | 17 | 22 | 19 | 25 | 23 | - | - | - | - | - |  |
| 2.5 | 24 | 23 | 30 | 26 | 34 | 31 | - | - | - | - | - |  |

Voltage Drop (Per Amp Per Meter)

| Nominal |  |  |  | 2 cables, single-phase a.c. |  |  |  | 3 or 4 cables, 3-phase a.c. |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Ref. Methods 3 |  | Ref. Methods 1 |  | Ref. Methods 3 |  | Ref. Methods 1, | Ref. Methods 1 and |  |
| Cross |  | 2 cables |  |  |  |  |  |  |  |  |  |  |
| Section |  | d.c. |  | and 4 (enclosed |  | and 11 (clipped |  | and 4 (enclosed |  |  | 11 |  |
|  |  |  |  | in conduit etc, |  | direct or on trays |  | in conduit etc, |  | 11 and 12 (in |  |  |
| Area |  |  |  |  |  |  |  |  |  |  | (Flat and touching) |  |
|  |  |  |  | in or on a wall) |  | touching) |  | in or on a wall) |  | trefoil) |  |  |
| 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 | 7 |  |
| mm2 |  | mV/A/m |  | mV/A/m |  | mV/A/m |  | mV/A/m |  | mV/A/m | mV/A/m |  |
| 1.5 |  | 31 |  | 31 |  | 27 |  | 27 |  | 27 | 27 |  |
| 2.5 |  | 19 |  | 19 |  | 16 |  | 16 |  | 16 | 16 |  |
|  | 300/500V |  | NBS5308 |  | Flame Retardancy |  | Reduced Fire Propagation |  |  |  |  |  |
|  | Rated Voltage |  |  |  | NF C32-070-2.1(C2) |  | NF C32-070-2.2(C1) |  |  |  |  |  |
|  |  |  | Standard |  | IEC60332-1-2/EN50265-2-1 |  | IEC60332-3-24/EN50266-2-4 |  |  |  |  |  |
|  |  |  |  |  |  |  | Zero |  |  |  |  |  |
|  |  |  | Low Corrosivity |  | Low Smoke Emission |  | Halogen Free |  |  |  |  |  |
|  |  |  | IEC60754-2 |  |  |  |  |  |  |  |  |  |
|  | Low Toxicity |  |  |  | IEC 61034-1&2 |  | IEC60754-1 |  |  |  |  |  |
|  |  |  | EN50267-2-2/3 |  |  |  |  |  |  |  |  |  |
|  | NES 02-713/NF C 20-454 |  | NF C 32-074 |  | EN 50268-1&2/NF C32-073 |  | EN50267-2-1 |  |  |  |  |  |