Caledonian

Flame Retardant Power & Control Cables

www.caledonian-cables.co.uk	www.addison-cables.com

600/1000V XLPE Insulated, LSZH Sheathed, Screened Power Cables (4 Cores)

FTX400 1RCZ1MZ1-R (CU/XLPE/CUTO/LSZH/SWA/LSZH 600/1000V Class 2)

APPLICATION

This cable is designed specifi cally to suit the broad spectrum of requirements of Variable Speed Drives and also include features for reducing the transmission of electromagnetic interference.

This range of screened cables drastically reduce interferences from electrical noise, especially in

Variable Speed Drive (VSD) applications and are manufactured with fixed conductors.

With shield conductivity of 1/10th of phase conductor conductivity, this range of VSD cables effectively restrain radiated and conducted radio-frequency emissions.

STANDARDS

Basic design adapted to IEC 60502-1

FIRE PERFORMANCE

| Flame Retardance (Single Vertical | EN 60332-1-2; IEC 60332-1-2; BS EN 60332-1-2; VDE |  |
| --- | --- | --- |
|  | 0482-332-1 ; NBN C 30-004 (cat. F1); NF C32-070-2.1(C2); |  |
| Wire Test) | CEI 20-35/1-2; EN 50265-2-1*; DIN VDE 0482-265-2-1* |  |
| Reduced Fire Propagation | EN 60332-3-24 (cat. C); IEC 60332-3-24; BS EN 60332-3-24; |  |
| (Vertically-mounted bundled wires | VDE 0482-332-3; NBN C 30-004 (cat. F2); NF C32-070-2.2(C1); |  |
| & cable test) | CEI 20-22/3-4; EN 50266-2-4*; DIN VDE 0482-266-2-4 |  |
| Halogen Free | IEC 60754-1; EN 50267-2-1; DIN VDE 0482-267-2-1; |  |
|  | CEI 20-37/2-1 ; BS 6425-1* |  |
| No Corrosive Gas Emission | IEC 60754-2; EN 50267-2-2; DIN VDE 0482-267-2-2; |  |
|  | CEI 20-37/2-2 ; BS 6425-2* |  |
| Minimum Smoke Emission | IEC 61034-1&2; EN 61034 -1&2; DIN VDE 0482-1034-1&2; |  |
|  | CEI 20-37/3-1&2; EN 50268-1&2*; BS 7622-1&2* |  |
| No Toxic gases | NES 02-713; NF C 20-454 |  |

Note: Asterisk * denotes superseded standard.

VOLTAGE RATING

600/1000V

CABLE CONSTRUCTION

ADDISON	65

ADDISON

Conductor: Plain annealed copper wire, stranded according to IEC(EN) 60228 class 2. Insulation: Extruded cross-linked XLPE compound.

Inner sheath1: LSZH Compound

Screen: Copper Tape

Inner sheath2: LSZH Compound

Armouring: Galvanised Steel Wire

Outer Sheath: Thermoplastic LSZH compound type LTS3 as per BS 7655-6.1 (Thermosetting LSZH compound type SW2-SW4 as per BS 7655-2.6 can be offered.). UV resistance, hydrocarbon resistance, oil resistance, anti rodent and anti termite properties can be offered as option.

COLOUR CODE

Insulation Colour as per BS7671

|  | With Earth Conductor | Without Earth Conductor |
| --- | --- | --- |
| 2Cores | - | Brown, Blue |
| 3Cores | Yellow/Green, Brown, Blue | Brown, Gray, Black |
| 4Cores | Yellow/Green, Brown, Gray, Black | Brown, Gray, Black, Blue |
| 5Cores | Yellow/Green, Brown, Gray, Black, Blue | Brown, Gray, Black, Blue, Black |
| Above 5 Cores | Yellow/Green, Black Numbered | Black Numbered |

Sheath Colour: Black (other colors upon request)

Physical AND THERMAL PROPERTIES

Temperature range during operation: Max.90°C for XLPE

250°C in short-circuit for 5s max. Minimum bending radius: 12 x Overall Diameter (for 1.5mm2 to 300mm2)

CONSTRUCTION PARAMETERS

|  | Conductor |  |  |  | FTX400 1RCZ1MZ1-R |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | No. of Core | No./ |  |  |  |  |  |  |  |  |
|  |  | Nominal | Nominal | Nominal | Diameter | Diameter | Armour | Nominal |  |  |
|  | X | Diameter | Insulation | Sheath | Under | Over Inner | Wire | Overall | Approx. |  |
|  | Cross |  |  |  |  |  |  |  | Weight |  |
|  |  | of | Thickness | Thickness | Screen | Sheath | Diameter | Diameter |  |  |
|  | Section | Strands |  |  |  |  |  |  |  |  |
|  | mm2 | No./mm | mm | mm | mm | mm | mm | mm | kg/km |  |
|  | 4x1.5 | 7/0.53 | 0.7 | 1.8 | 9.7 | 12.1 | 13.9 | 17.7 | 640 |  |
|  | 4x2.5 | 7/0.67 | 0.7 | 1.8 | 10.7 | 13.1 | 14.9 | 18.7 | 730 |  |
|  | 4x4 | 7/0.85 | 0.7 | 1.8 | 12.0 | 14.4 | 16.2 | 20.0 | 870 |  |
|  | 4x6 | 7/1.04 | 0.7 | 1.8 | 13.4 | 15.8 | 18.3 | 22.1 | 1180 |  |
|  | 4x10 | 7/1.35 | 0.7 | 1.8 | 15.6 | 18.0 | 20.5 | 24.3 | 1490 |  |
|  | 4x16 | 7/1.70 | 0.7 | 1.8 | 18.1 | 20.5 | 23.7 | 27.5 | 2070 |  |
|  | 4x25 | 7/2.14 | 0.9 | 1.8 | 22.3 | 24.1 | 27.3 | 31.1 | 2790 |  |
|  | 4x35(S) | 7/2.52 | 0.9 | 1.8 | 25.0 | 26.8 | 30.0 | 33.8 | 2940 |  |
|  | 4x50(S) | 19/1.78 | 1.0 | 2.0 | 27.8 | 29.6 | 32.8 | 37.0 | 3500 |  |
|  | 4x70(S) | 19/2.14 | 1.1 | 2.2 | 31.6 | 33.4 | 37.4 | 42.0 | 5000 |  |
| 66 | Caledonian |  |  |  |  |  |  |  |  |  |

Caledonian

Flame Retardant Power & Control Cables

www.caledonian-cables.co.uk	www.addison-cables.com

| 4x95(S) | 19/2.52 | 1.1 | 2.3 | 35.4 | 37.2 | 41.2 | 46.0 | 6300 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 4x120(S) | 37/2.03 | 1.2 | 2.5 | 39.0 | 40.8 | 45.8 | 51.0 | 8200 |
| 4x150(S) | 37/2.25 | 1.4 | 2.6 | 42.0 | 43.8 | 48.8 | 54.2 | 9600 |
| 4x185(S) | 37/2.52 | 1.6 | 2.8 | 47.8 | 49.6 | 54.6 | 60.4 | 11500 |
| 4x240(S) | 61/2.25 | 1.7 | 3.0 | 54.0 | 55.8 | 60.8 | 67.0 | 14400 |
| 4x300(S) | 61/2.52 | 1.8 | 3.0 | 58.0 | 59.8 | 64.8 | 71.4 | 17200 |

(S) : Sectoral Stranded Conductors.

Electrical PROPERTIES

Conductor Operating Temperature : 90°C

Ambient Temperature : 30°C

Current-Carrying Capacities (Amp)

|  |  |  | Reference Method |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Reference Method |  | 11 (on a perforated |  | In single-way |  | Laid direct in |  |  |
|  | 1 (clipped |  | horizontal cable trayor |  |  |  |  |  |  |
|  |  |  |  |  | ducts |  | ground |  |  |
| Conductor | direct) |  | Reference Method 13 |  |  |  |  |  |  |
|  |  |  | [free air] ) |  |  |  |  |  |  |
| cross- |  |  |  |  |  |  |  |  |  |
|  | one |  |  |  | one |  | one |  |  |
| sectional |  | one |  |  |  | one |  | one |  |
|  | 2-core |  |  | one 3-core | 2-core |  | 2-core |  |  |
| area |  | 3-core or | one 2-core |  |  | 3-core or |  | 3-core or |  |
|  | cable | 4-core | cable single | or 4-core | cable | 4-core | cable | 4-core |  |
|  | single |  |  | cable | single |  | single |  |  |
|  |  | cable | phase a.c. |  |  | cable |  | cable |  |
|  | phase |  |  | 3-phase | phase |  | phase |  |  |
|  |  | 3-phase | or d.c. |  |  | 3-phase |  | 3-phase |  |
|  | a.c. or | a.c. |  | a.c. | a.c. or | a.c. | a.c. or | a.c. |  |
|  | d.c. |  |  |  | d.c. |  | d.c. |  |  |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |  |
| mm2 | A | A | A | A | A | A | A | A |  |
| 1.5 | 27 | 23 | 29 | 25 | - | 23 | - | 28 |  |
| 2.5 | 36 | 31 | 39 | 33 | - | 30 | - | 36 |  |
| 4 | 49 | 42 | 52 | 44 | - | 40 | - | 48 |  |
| 6 | 62 | 53 | 66 | 56 | - | 50 | - | 60 |  |
| 10 | 85 | 73 | 90 | 78 | - | 65 | - | 80 |  |
| 16 | 110 | 94 | 115 | 99 | 115 | 94 | 140 | 115 |  |
| 25 | 146 | 124 | 152 | 131 | 145 | 125 | 180 | 150 |  |
| 35 | 180 | 154 | 188 | 162 | 175 | 150 | 215 | 180 |  |
| 50 | 219 | 187 | 228 | 197 | 210 | 175 | 255 | 215 |  |
| 70 | 279 | 238 | 291 | 251 | 260 | 215 | 315 | 265 |  |
| 95 | 338 | 289 | 354 | 304 | 310 | 260 | 380 | 315 |  |
| 120 | 392 | 335 | 410 | 353 | 355 | 300 | 430 | 360 |  |
| 150 | 451 | 386 | 472 | 406 | 400 | 335 | 480 | 405 |  |
| 185 | 515 | 441 | 539 | 463 | 455 | 380 | 540 | 460 |  |
| 240 | 607 | 520 | 636 | 546 | 520 | 440 | 630 | 530 |  |
| 300 | 698 | 599 | 732 | 628 | 590 | 495 | 700 | 590 |  |

ADDISON	67

ADDISON

Voltage Drop (Per Amp Per Meter)

| Conductor |  |  |  |  |  |  |  |  | 2 cables, | 3 or 4 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 2-core | 2 cables, single-phase 3 or 4 cables, 3-phase |  |  |  |  |  |  | single-phase | cables, |  |
| cross- |  |  |  |  |  |  |  |  |  |  |  |
| sectional | cable d.c. |  |  | a.c. |  |  | a.c. |  | a.c. | 3-phase a.c. |  |
|  |  |  |  |  |  |  |  |  | In ducts or | In ducts or |  |
| area |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | in ground | in ground |  |
| 1 | 2 |  |  | 3 |  |  | 4 |  | 5 | 6 |  |
| mm2 | mV/A/m |  |  | mV/A/m |  |  | mV/A/m |  | mV/A/m | mV/A/m |  |
| 1.5 | 31.0 |  |  | 31.0 |  |  | 27.0 |  | 31.0 | 25.0 |  |
| 2.5 | 19.0 |  |  | 19.0 |  |  | 16.0 |  | 19.0 | 15.0 |  |
| 4 | 12.0 |  |  | 12.0 |  |  | 10.0 |  | 12.0 | 9.7 |  |
| 6 | 7.9 |  |  | 7.9 |  |  | 6.8 |  | 7.9 | 6.5 |  |
| 10 | 4.7 |  |  | 4.7 |  |  | 4.0 |  | 4.7 | 3.9 |  |
| 16 | 2.9 |  |  | 2.9 |  |  | 2.5 |  | 2.9 | 2.6 |  |
|  |  |  | r | x | z | r | x | z |  |  |  |
| 25 | 1.850 | 1.350 |  | 0.160 | 1.900 | 1.600 | 0.140 | 1.650 | 1.900 | 1.600 |  |
| 35 | 1.350 | 1.350 |  | 0.155 | 1.350 | 1.150 | 0.135 | 1.150 | 1.350 | 1.200 |  |
| 50 | 0.980 | 0.990 |  | 0.155 | 1.000 | 0.860 | 0.135 | 0.870 | 1.000 | 0.870 |  |
| 70 | 0.670 | 0.670 |  | 0.150 | 0.690 | 0.590 | 0.130 | 0.600 | 0.690 | 0.610 |  |
| 95 | 0.490 | 0.500 |  | 0.150 | 0.520 | 0.430 | 0.130 | 0.450 | 0.520 | 0.450 |  |
| 120 | 0.390 | 0.400 |  | 0.145 | 0.420 | 0.340 | 0.130 | 0.370 | 0.420 | 0.360 |  |
| 150 | 0.310 | 0.320 |  | 0.145 | 0.350 | 0.280 | 0.125 | 0.300 | 0.350 | 0.300 |  |
| 185 | 0.250 | 0.260 |  | 0.145 | 0.290 | 0.220 | 0.125 | 0.260 | 0.290 | 0.250 |  |
| 240 | 0.195 | 0.200 |  | 0.140 | 0.240 | 0.175 | 0.125 | 0.210 | 0.240 | 0.210 |  |
| 300 | 0.155 | 0.160 |  | 0.140 | 0.210 | 0.140 | 0.120 | 0.185 | 0.210 | 0.190 |  |
| Note : |  |  |  |  |  |  |  |  |  |  |  |
| r = conductor resistance at operating temperature |  |  |  |  |  |  |  |  |  |  |  |
| x = reactance |  |  |  |  |  |  |  |  |  |  |  |
| z = impedance |  |  |  |  |  |  |  |  |  |  |  |
| 600/1000V | IECN60502-1 |  |  | Flame Retardancy |  | Reduced Fire Propagation |  |  |  |  |  |
|  |  |  |  |  |  | NF C32-070-2.2(C1) |  |  |  |  |  |
| Rated Voltage | Standard |  |  | NF C32-070-2.1(C2) |  | IEC60332-3-24 |  |  |  |  |  |
|  |  |  |  | IEC60332-1-2/EN50265-2-1 |  | EN50266-2-4 |  |  |  |  |  |
|  |  |  |  |  |  | Zero |  |  |  |  |  |
|  | Low Corrosivity |  |  | Low Smoke Emission |  | Halogen Free |  |  |  |  |  |
| Low Toxicity | IEC60754-2 |  |  | IEC 61034-1&2 |  | IEC60754-1 |  |  |  |  |  |
|  | EN50267-2-2/3 |  |  |  |  |  |  |  |  |  |  |
| NES 02-713/NF C 20-454 |  |  | EN 50268-1&2/NF C32-073 |  |  | EN50267-2-1 |  |  |  |  |  |
|  | NF C 32-074 |  |  |  |  |  |  |  |  |  |  |

68	Caledonian