ADDISON

450/750V XLPE Insulated, LSZH Sheathed Power Cables (2-4 Cores)

FTX200 07RZ1-R (CU/XLPE/LSZH 450/750V Class 2)

Plain Annealed Copper

XLPE Insulation

Filler

LSZH Outer Sheath

APPLICATION

The cables is mainly used in power stations, mass transit underground passenger systems, airports, petrochemical plants, hotels, hospitals, and high-rise buildings.

STANDARDS

Basic design adapted to BS 7211; IEC 60502-1

FIRE PERFORMANCE

| Flame Retardance (Single Vertical | EN 60332-1-2; IEC 60332-1-2; BS EN 60332-1-2; VDE 0482-332-1 ; |  |
| --- | --- | --- |
|  | NBN C 30-004 (cat. F1); NF C32-070-2.1(C2); |  |
| Wire Test) |  |  |
|  | CEI 20-35/1-2; EN 50265-2-1*; DIN VDE 0482-265-2-1* |  |
| Reduced Fire Propagation | EN 60332-3-24 (cat. C); IEC 60332-3-24; BS EN 60332-3-24; VDE |  |
| (Vertically-mounted bundled wires & | 0482-332-3; NBN C 30-004 (cat. F2); NF C32-070-2.2(C1); CEI |  |
| cable test) | 20-22/3-4; EN 50266-2-4*; DIN VDE 0482-266-2-4 |  |
| Halogen Free | IEC 60754-1; EN 50267-2-1; DIN VDE 0482-267-2-1; |  |
|  | CEI 20-37/2-1 ; BS 6425-1* |  |
| No Corrosive Gas Emission | IEC 60754-2; EN 50267-2-2; DIN VDE 0482-267-2-2; |  |
|  | CEI 20-37/2-2 ; BS 6425-2* |  |
| Minimum Smoke Emission | IEC 61034-1&2; EN 61034 -1&2; DIN VDE 0482-1034-1&2; |  |
|  | CEI 20-37/3-1&2; EN 50268-1&2*; BS 7622-1&2* |  |
| No Toxic gases | NES 02-713; NF C 20-454 |  |

Note: Asterisk * denotes superseded standard.

VOLTAGE RATING

450/750V

CABLE CONSTRUCTION

Conductor: Plain annealed copper wire, stranded according to IEC(EN) 60228 class 2. Insulation: Extruded cross-linked XLPE compound.

22	Caledonian

Caledonian

Flame Retardant Power & Control Cables

www.caledonian-cables.co.uk	www.addison-cables.com

Filler, binder (if any): PP, PET

Outer Sheath: Thermoplastic LSZH compound type LTS3 as per BS 7655-6.1 (Thermosetting LSZH compound type SW2-SW4 as per BS 7655-2.6 can be offered.). UV resistance, hydrocarbon resistance, oil resistance, anti rodent and anti termite properties can be offered as option.

COLOUR CODE

Insulation Colour as per BS7671

|  | With Earth Conductor | Without Earth Conductor |
| --- | --- | --- |
| 2Cores | - | Brown, Blue |
| 3Cores | Yellow/Green, Brown, Blue | Brown, Gray, Black |
| 4Cores | Yellow/Green, Brown, Gray, Black | Brown, Gray, Black, Blue |
| 5Cores | Yellow/Green, Brown, Gray, Black, Blue | Brown, Gray, Black, Blue, Black |
| Above 5 Cores | Yellow/Green, Black Numbered | Black Numbered |

Sheath Colour: Black (other colors upon request)

Physical AND THERMAL PROPERTIES

Temperature range during operation: Max.90°C for XLPE

250°C in short-circuit for 5s max.

Minimum bending radius: 6 x Overall Diameter

CONSTRUCTION PARAMETER

|  | Conductor |  |  | FTX200 07RZ1-R |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| No. of | No./Nominal | Nominal | Nominal | Nominal | Nominal | Max.DC |  |  |
| Core X | Diameter of | Overall | Insulation | Sheath | Overall | resistance | Approx. |  |
| Cross |  | Diameter |  |  |  | of conductor | Weight |  |
| Section | Strands | Conductor | Thickness | Thickness | Diameter | @20°C |  |  |
| Noxmm2 | No./mm | mm | mm | mm | mm | Ω/km | kg/km |  |
| 2x1.0 | 7/0.44 | 1.32 | 0.7 | 1.2 | 8.5 | 18.1 | 101 |  |
| 2x1.5 | 7/0.53 | 1.59 | 0.7 | 1.2 | 9.1 | 12.1 | 120 |  |
| 2x2.5 | 7/0.67 | 2.01 | 0.7 | 1.2 | 10.0 | 7.41 | 154 |  |
| 2x4.0 | 7/0.85 | 2.55 | 0.7 | 1.3 | 11.1 | 4.61 | 205 |  |
| 3x1.0 | 7/0.44 | 1.32 | 0.7 | 1.2 | 9.0 | 18.1 | 118 |  |
| 3x1.5 | 7/0.53 | 1.59 | 0.7 | 1.2 | 9.6 | 12.1 | 142 |  |
| 3x2.5 | 7/0,67 | 2.01 | 0.7 | 1.2 | 10.6 | 7.41 | 185 |  |
| 3x4.0 | 7/0.85 | 2.55 | 0.7 | 1.3 | 11.8 | 4.61 | 251 |  |
| 4x1.0 | 7/0.44 | 1.32 | 0.7 | 1.2 | 9.8 | 18.1 | 141 |  |
| 4x1.5 | 7/0.53 | 1.59 | 0.7 | 1.2 | 10.5 | 12.1 | 171 |  |
| 4x2.5 | 7/0.67 | 2.01 | 0.7 | 1.3 | 11.6 | 7.41 | 226 |  |
| 4x4.0 | 7/0.85 | 2.55 | 0.7 | 1.3 | 13.0 | 4.61 | 309 |  |

Electrical PROPERTIES

Conductor Operating Temperature : 90°C

ADDISON	23

ADDISON

Ambient Temperature : 30°C

Current-Carrying Capacities (Amp)

|  |  |  |  |  |  |  |  |  |  | Reference |  |  |  |  |  |  |  |  |  |  | Reference |  |  |  | Reference Method 12 (free |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Conductor |  |  | Reference Method |  |  |  |  |  |  | Method 3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | air) |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Method 11 (on a |  |  |  |  |  |  |  |  |  |  |  |
| cross- |  |  |  | 4 (enclosed in |  |  |  |  |  | (enclosed in |  |  |  |  |  | Reference Method |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| sectional |  |  | conduit in thermally |  |  |  |  |  |  | conduit on |  |  |  |  |  | 1 (clipped direct) |  |  |  |  | perforated cable |  |  |  | Horizontal |  |  |  | Vertical |  |  |  |
| area |  |  | insulating wall etc) |  |  |  |  |  |  | a wall or in |  |  |  |  |  |  |  |  |  |  | tray, horizontal or |  |  |  |  | flat |  |  | flat | Trefoil |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | vertical) |  |  |  | spaced |  |  |  | spaced |  |  |  |
|  |  |  |  |  |  |  |  |  |  | trunking etc) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 2 cables, |  |  |  | 2 cables, |  |  |  |
|  |  |  | 2 |  |  |  |  |  |  | 2 |  |  |  |  |  | 2 cables, |  |  |  | 3 or 4 | 2 cables, |  | 3 or 4 |  | single- |  |  |  | single- | 3 |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | single- |  |  |  | cables, | single- |  | cables, |  | phase |  |  |  | phase |  |  |  |
|  |  |  | cables, |  |  |  |  | 3 or 4 |  | cables, |  |  |  | 3 or 4 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | cables, |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | phase |  |  |  | 3-phase | phase |  | 3-phase |  | a.c. or |  |  |  | a.c. or |  |  |  |
|  |  |  | single- |  |  |  |  | cables, |  | single- |  |  |  | cables, |  | a.c. or |  |  |  | a.c. flat | a.c. or |  | a.c. flat |  |  | d.c. |  |  | d.c. | trefoil |  |  |
|  |  |  | phase |  |  |  |  | 3-phase |  | phase |  |  |  | 3-phase |  | d.c. flat |  |  |  | and | d.c. or |  | and |  | or 3 c |  |  |  | or 3 | 3- |  |  |
|  |  |  | a.c. or |  |  |  |  | a.c. |  | a.c. or |  |  |  | a.c. |  | and |  |  |  | touching | flat | and | touching |  | ables |  |  |  | cables | phase |  |  |
|  |  |  |  | d.c. |  |  |  |  |  | d.c |  |  |  |  |  | touching |  |  |  | or trefoil | touching |  | or trefoil |  | three |  |  |  | three | a.c. |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | phase |  |  |  | phase |  |  |  |
| 1 |  |  | 2 |  |  |  |  | 3 |  | 4 |  |  |  | 5 |  | 6 |  |  |  | 7 | 8 |  | 9 |  |  | 10 |  |  | 11 | 12 |  |  |
| mm2 |  |  |  | A |  |  |  | A |  | A |  |  |  | A |  | A |  |  |  | A | A |  | A |  |  | A |  |  | A | A |  |  |
| 1.0 |  |  | 13 |  |  |  |  | - |  | - |  |  |  | - |  | 15 |  |  |  | - | - |  | - |  |  | - |  |  | - | - |  |  |
| 1.5 |  |  | 18 |  |  |  |  | 17 |  | 22 |  |  |  | 19 |  | 25 |  |  |  | 23 | - |  | - |  |  | - |  |  | - | - |  |  |
| 2.5 |  |  | 24 |  |  |  |  | 23 |  | 30 |  |  |  | 26 |  | 34 |  |  |  | 31 | - |  | - |  |  | - |  |  | - | - |  |  |
| 4 |  |  | 33 |  |  |  |  | 30 |  | 40 |  |  |  | 35 |  | 46 |  |  |  | 41 | - |  | - |  |  | - |  |  | - | - |  |  |
| Voltage Drop (Per Amp Per Meter) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Nominal |  |  |  |  |  |  | 2 cables, single-phase a.c. |  |  |  |  |  |  |  |  |  |  |  |  |  | 3 or 4 cables, 3-phase a.c. |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | Ref. Methods 3 |  |  |  |  |  | Ref. Methods 1 |  |  |  |  |  | Ref. Methods 3 |  |  |  |  |  |  |  |  | Ref. Methods 1 and |  |  |  |  |
| Cross |  |  | 2 cables |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Ref. Methods 1, |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | and 4 (enclosed |  |  |  |  |  | and 11 (clipped |  |  |  |  |  | and 4 (enclosed |  |  |  |  |  |  |  |  |  | 11 |  |  |  |
| Section |  |  |  | d.c. |  |  | in conduit etc, |  |  |  |  |  | direct or on trays |  |  |  |  |  | in conduit etc, |  |  | 11 and 12 (in |  |  |  |  |  |  |  |  |  |  |
| Area |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | (Flat and touching) |  |  |  |  |
|  |  |  |  |  |  |  | in or on a wall) |  |  |  |  |  |  | touching) |  |  |  |  | in or on a wall) |  |  |  | trefoil) |  |  |  |  |  |  |  |  |  |
| 1 |  |  | 2 |  |  |  | 3 |  |  |  |  |  |  | 4 |  |  |  |  |  | 5 |  |  | 6 |  |  |  |  |  | 7 |  |  |  |
| mm2 |  |  | mV/A/m |  |  |  | mV/A/m |  |  |  |  |  |  | mV/A/m |  |  |  |  |  | mV/A/m |  |  | mV/A/m |  |  |  |  |  | mV/A/m |  |  |  |
| 1.0 |  |  | 46 |  |  |  | 46 |  |  |  |  |  |  | - |  |  |  |  |  | - |  |  | - |  |  |  |  |  | - |  |  |  |
| 1.5 |  |  | 31 |  |  |  | 31 |  |  |  |  |  |  | 27 |  |  |  |  |  | 27 |  |  | 27 |  |  |  |  |  | 27 |  |  |  |
| 2.5 |  |  | 19 |  |  |  | 19 |  |  |  |  |  |  | 16 |  |  |  |  |  | 16 |  |  | 16 |  |  |  |  |  | 16 |  |  |  |
| 4 |  |  | 33 |  |  |  | 12 |  |  |  |  |  |  | 10 |  |  |  |  |  | 10 |  |  | 10 |  |  |  |  |  | 10 |  |  |  |
|  |  | 450/750V |  |  |  |  | NBS7211 |  |  |  |  |  | IECN60502-1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Flame Retardancy |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Reduced Fire Propagation |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | NF C32-070-2.2(C1) |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | NF C32-070-2.1(C2) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Rated Voltage |  |  |  |  |  |  | Standard |  |  |  |  |  | Standard |  |  |  |  |  |  |  |  | IEC60332-3-24 |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | IEC60332-1-2/EN50265-2-1 |  |  |  |  |  | EN50266-2-4 |  |  |  |  |  |  |  |  |  |  |

Zero

|  | Low Corrosivity | Low Smoke Emission |  |
| --- | --- | --- | --- |
|  | IEC60754-2 |  |  |
| Low Toxicity |  | IEC 61034-1&2 |  |
|  | EN50267-2-2/3 |  |  |
| NES 02-713/NF C 20-454 | NF C 32-074 | EN 50268-1&2/NF C32-073 |  |

Halogen Free IEC60754-1/ EN50267-2-1

24	Caledonian