BS 6883&BS 7917 Caledonian Offshore & Marine Cables

LV Fire Resistant Power & Control Cables

www.caledonian-cables.co.uk

  - /1kV HF-EPR Insulated, SW2/SW4 Sheathed Unarmoured Fire Resistant Power & Control Cables

Application

These ﬁre resistant elastomeric insulated cables are designed for ﬁxed wiring in ships and on mobile offshore units, suitable for use in power and control applications where ﬁre integrity is essential.

Standards

	BS 7917

    - IEC 60331-31 Fire resistant

    - IEC 60332-3A Flame retardant

	IEC 60754-1; IEC 60754-2

Corrosivity

    - IEC 61034-2 Smoke density

    - Cold bend and impact (-40°C) (on request)

    - CSA C22.2 No. 38-95 (on request)

Construction

Stranded Tinned Copper Conductor Mica Tape+HF-EPR GP4 Insulation SW2/SW4 Outer Sheath

    - Conductor: Tinned copper wire stranded circular cl. 2 BS 6360/IEC 60228.

    - Insulation: Mica tape + HF-EPR GP4 according to BS 7655 1.2.

    - Sheath: Halogen free thermosetting compound SW4 according to BS 7655 2.6 or reduced halogen thermosetting compound SW2 according to BS 7655 2.6.

Mechanical and Thermal Properties

Minimum Internal Bending Radius: 6×OD (OD>25mm); 4×OD (OD ≤25mm) Temperature Range: -40℃ ~ +90℃

24	ADDISON	www.addison-cables.com

BS 6883&BS 7917 Caledonian Offshore & Marine Cables

LV Fire Resistant Power & Control Cables

www.caledonian-cables.co.uk

Dimensions and Weight

Single core cables

| Construction No. of cores×Cross section(mm²) | Nominal Insulation Thickness mm | Nominal Sheath Thickness mm | Minimum Overall Diameter mm | Maximum Overall Diameter mm | Approx. Weight kg/km |
| --- | --- | --- | --- | --- | --- |
| 1×4 | 1.0 | 1.0 | 6.7 | 8.0 | 90 |
| 1×6 | 1.0 | 1.0 | 7.2 | 8.5 | 135 |
| 1×10 | 1.0 | 1.0 | 8.1 | 9.5 | 180 |
| 1×16 | 1.0 | 1.1 | 9.3 | 10.7 | 315 |
| 1×25 | 1.2 | 1.2 | 11.5 | 13.2 | 550 |
| 1×35 | 1.2 | 1.2 | 12.3 | 14.1 | 715 |
| 1×50 | 1.4 | 1.3 | 14.1 | 15.9 | 830 |
| 1×70 | 1.4 | 1.3 | 15.8 | 17.8 | 1110 |
| 1×95 | 1.6 | 1.4 | 18.1 | 20.2 | 1470 |
| 1×120 | 1.6 | 1.5 | 20.0 | 22.4 | 2130 |
| 1×150 | 1.8 | 1.6 | 22.0 | 24.6 | 2475 |
| 1×185 | 2.0 | 1.7 | 24.4 | 27.0 | 2870 |
| 1×240 | 2.2 | 1.8 | 27.5 | 30.3 | 3120 |
| 1×300 | 2.4 | 1.9 | 30.4 | 33.6 | 4060 |

Multicore cables

| Construction No. of cores×Cross section(mm²) | Nominal Insulation Thickness mm | Nominal Sheath Thickness mm | Minimum Overall Diameter mm | Maximum Overall Diameter mm | Approx. Weight kg/km |
| --- | --- | --- | --- | --- | --- |
| 2×1.5 | 0.8 | 1.1 | 9.0 | 10.4 | 145 |
| 2×2.5 | 0.8 | 1.1 | 9.8 | 11.4 | 180 |
| 2×4 | 1.0 | 1.2 | 11.8 | 13.5 | 260 |
| 2×6 | 1.0 | 1.2 | 12.9 | 14.6 | 325 |
| 2×10 | 1.0 | 1.3 | 14.9 | 16.8 | 445 |
| 2×16 | 1.0 | 1.4 | 17.1 | 19.1 | 630 |
| 2×25 | 1.2 | 1.5 | 21.2 | 23.7 | 930 |
| 2×35 | 1.2 | 1.6 | 23.1 | 25.7 | 1210 |
| 2×50 | 1.4 | 1.7 | 26.5 | 29.2 | 1630 |
| 2×70 | 1.4 | 1.9 | 30.3 | 33.5 | 2210 |
| 2×95 | 1.6 | 2.1 | 34.9 | 38.2 | 3010 |
| 2×120 | 1.6 | 2.2 | 38.4 | 42.2 | 3690 |
| 3×1.5 | 0.8 | 1.1 | 9.6 | 11.0 | 170 |
| 3×2.5 | 0.8 | 1.1 | 10.4 | 12.1 | 210 |
| 3×4 | 1.0 | 1.2 | 12.6 | 14.3 | 310 |
| 3×6 | 1.0 | 1.2 | 13.8 | 15.5 | 395 |
| 3×10 | 1.0 | 1.3 | 15.9 | 17.8 | 590 |
| 3×16 | 1.0 | 1.4 | 18.2 | 20.3 | 830 |
| 3×25 | 1.2 | 1.6 | 22.9 | 25.4 | 1270 |
| 3×35 | 1.2 | 1.7 | 24.9 | 27.6 | 1540 |

www.addison-cables.com

ADDISON	25

BS 6883&BS 7917 Caledonian Offshore & Marine Cables

LV Fire Resistant Power & Control Cables

www.caledonian-cables.co.uk

| Construction No. of cores×Cross section(mm²) | Nominal Insulation Thickness mm | Nominal Sheath Thickness mm | Minimum Overall Diameter mm | Maximum Overall Diameter mm | Approx. Weight kg/km |
| --- | --- | --- | --- | --- | --- |
| 3×50 | 1.4 | 1.8 | 28.5 | 31.3 | 2100 |
| 3×70 | 1.4 | 2.0 | 32.7 | 35.9 | 2870 |
| 3×95 | 1.6 | 2.2 | 37.5 | 41.0 | 3910 |
| 3×120 | 1.6 | 2.3 | 41.3 | 45.3 | 4800 |
| 3×150 | 1.8 | 2.5 | 45.8 | 49.9 | 5810 |
| 3×185 | 2.0 | 2.7 | 50.9 | 55.5 | 7290 |
| 3×240 | 2.2 | 2.9 | 57.5 | 62.4 | 9440 |
| 4×1.5 | 0.8 | 1.1 | 10.5 | 12.1 | 200 |
| 4×2.5 | 0.8 | 1.1 | 11.4 | 13.1 | 250 |
| 4×4 | 1.0 | 1.2 | 13.8 | 15.6 | 375 |
| 4×6 | 1.0 | 1.3 | 15.3 | 17.3 | 495 |
| 4×10 | 1.0 | 1.4 | 17.7 | 19.7 | 740 |
| 4×16 | 1.0 | 1.5 | 20.3 | 22.8 | 1050 |
| 4×25 | 1.2 | 1.7 | 25.5 | 28.1 | 1580 |
| 4×35 | 1.2 | 1.8 | 27.7 | 30.5 | 1960 |
| 4×50 | 1.4 | 1.9 | 31.8 | 35.0 | 2570 |
| 4×70 | 1.4 | 2.1 | 36.3 | 39.7 | 3530 |
| 4×95 | 1.6 | 2.3 | 41.7 | 45.7 | 4850 |
| 4×120 | 1.6 | 2.5 | 46.2 | 50.3 | 5990 |
| 5×1.5 | 0.8 | 1.1 | 11.4 | 13.1 | 220 |
| 7×1.5 | 0.8 | 1.2 | 12.6 | 14.4 | 285 |
| 12×1.5 | 0.8 | 1.3 | 16.8 | 18.8 | 465 |
| 19×1.5 | 0.8 | 1.4 | 19.9 | 22.4 | 680 |
| 27×1.5 | 0.8 | 1.6 | 24.3 | 26.9 | 960 |
| 37×1.5 | 0.8 | 1.7 | 27.4 | 30.4 | 1260 |
| 5×2.5 | 0.8 | 1.2 | 12.7 | 14.4 | 310 |
| 7×2.5 | 0.8 | 1.2 | 13.9 | 15.6 | 375 |
| 12×2.5 | 0.8 | 1.4 | 18.7 | 20.8 | 610 |
| 19×2.5 | 0.8 | 1.5 | 22.1 | 24.7 | 895 |

26	ADDISON	www.addison-cables.com