NEK606	Water Blocked

Offshore & Marine Cables

Water Blocked P7 or P7/P14 BFOU 6/10kV

Applications

These cables are partially water blocked, fire resistant, flame retardant, low smoke,

halogen free and mud resistant, used for fixed installation for medium voltage power.

Standards

	IEC 60092-354

	IEC 60092-351

	IEC 60092-359

	IEC 60331-21

	IEC 60332-1

	IEC 60332-3-22

	IEC 60754-1,2

	IEC 61034-1,2

	NEK 606:2004

- VG 95218 part 29

Construction

Polyurethane Outer Sheath Water Blocking Tape Water Blocking Fillers Halogen-free Bedding

Stranded Copper Conductor Mica Tape + HFEPR Insulation Conductor Screen

Insulation Screen Copper Wire Braid

SHF2/SHF MUD Inner Sheath

- Conductors: Circular tinned annealed stranded copper to IEC 60228 class 2.

- Conductor Screen: Semi conducting material.

- Insulation: Mica tape + Halogen free EPR.

- Insulation Screen: Semi conducting material and tinned copper wire braid.

- Filler: Water blocking fillers, if required.

- Bedding: Halogen free compound, PETP wrapping tape will be applied over the bedding, if required.

- Armour: Tinned copper wire braid, PETP wrapping tape will be applied over the

braiding, if required.

- Water Blocking Elements: Water blocking tape and strings for providing longitudinal

water tightness.

- Inner Sheath: Halogen free thermosetting compound, SHF2 (for TYPE P7), or halogen free mud resistant thermosetting compound, SHF MUD (for TYPE P7/P14), coloured red.

- Outer Sheath: Polyurethane for providing transversal water tightness, PE is optional,but can not meet low smoke standard.

www.caledonian-cables.co.uk

www.caledonian-cables.com 	45

NEK606	Water Blocked

Offshore & Marine Cables

Electrical Characteristics

| Nominal Cross Section Area | mm² | 25 |  | 35 |  | 50 |  | 70 |  | 95 |  | 120 |  | 150 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Nominal Conductor Diameter | mm | 6.5 |  | 7.4 |  | 8.7 |  | 10.3 |  | 12.2 |  | 13.8 |  | 15.1 |
| Maximum DC Resistant@20˚C | Ω/km | 0.734 |  | 0.529 |  | 0.391 |  | 0.27 |  | 0.195 |  | 0.154 |  | 0.126 |
| Continuous Current Rating@45˚C 1 Core | A | 127 |  | 157 |  | 196 |  | 242 |  | 293 |  | 339 |  | 389 |
| Continuous Current Rating@45˚C 3 Core | A | 89 |  | 110 |  | 137 |  | 169 |  | 205 |  | 237 |  | 272 |
| Short Circuit Current 1s | A | 3580 |  | 5010 |  | 7150 |  | 10020 |  | 13590 |  | 17170 |  | 21460 |
| Operating Voltage | KV | 6/10 |  | 6/10 |  | 6/10 |  | 6/10 |  | 6/10 |  | 6/10 |  | 6/10 |
| Nominal Cross Section Area | mm² |  | 185 |  | 240 |  | 300 |  | 400 |  | 500 |  | 630 |  |
| Nominal Conductor Diameter | mm |  | 17.0 |  | 19.6 |  | 21.9 |  | 24.5 |  | 27.5 |  | 32.3 |  |
| Maximum DC Resistant@20˚C | Ω/km |  | 0.1 |  | 0.0762 |  | 0.0607 |  | 0.0475 |  | 0.0369 |  | 0.0286 |  |
| Continuous Current Rating@45˚C 1 Core | A |  | 444 |  | 522 |  | 601 |  | 690 |  | 780 |  | 890 |  |
| Continuous Current Rating@45˚C 3 Core | A |  | 311 |  | 365 |  | 421 |  | 483 |  | 546 |  | 623 |  |
| Short Circuit Current 1s | A |  | 26470 |  | 34340 |  | 42930 |  | 57230 |  | 71540 |  | 90140 |  |
| Operating Voltage | KV |  | 6/10 |  | 6/10 |  | 6/10 |  | 8.7/15 |  | 8.7/15 |  | 8.7/15 |  |

Ambient Temperature Correction Factors

| Ambient Temperature Correction Factors | 35 | 40 | 45 | 50 | 55 | 60 | 65 | 70 | 75 | 80 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Rating Factor | 1.1 | 1.05 | 1.0 | 0.94 | 0.88 | 0.82 | 0.74 | 0.67 | 0.58 | 0.47 |

Mechanical and Thermal Properties

- Bending Radius: 15×OD (during installation); 9×OD (fixed installed)

- Temperature Range: -20˚C ~ +90˚C

Dimensions and Weight

| Construction No. of cores×Cross section(mm²) | Nominal Insulation Thickness mm | Nominal Bedding Thickness mm | Nominal Inner Sheath Thickness mm | Nominal Outer Sheath Thickness mm | Nominal Overall Diameter mm | Nominal Weight kg/km |
| --- | --- | --- | --- | --- | --- | --- |
| 1×16 | 3.4 | 1.5 | 1.2 | 1.0 | 27.6±2 | 1040 |
| 1×25 | 3.4 | 1.6 | 1.2 | 1.2 | 29.5±2 | 1208 |
| 1×35 | 3.4 | 1.7 | 1.2 | 1.2 | 30.9±2 | 1386 |
| 1×50 | 3.4 | 1.7 | 1.3 | 1.2 | 32.3±2 | 1575 |

46	www.addison-tech.com

www.addison-cables.com

NEK606	Water Blocked

Offshore & Marine Cables

| Construction No. of cores×Cross section(mm²) | Nominal Insulation Thickness mm | Nominal Bedding Thickness mm | Nominal Inner Sheath Thickness mm | Nominal Outer Sheath Thickness mm | Nominal Overall Diameter mm | Nominal Weight kg/km |
| --- | --- | --- | --- | --- | --- | --- |
| 1×70 | 3.4 | 1.8 | 1.3 | 1.2 | 34.3±2 | 1901 |
| 1×95 | 3.4 | 1.8 | 1.4 | 1.4 | 36.8±2 | 2268 |
| 1×120 | 3.4 | 1.9 | 1.4 | 1.4 | 38.9±2 | 2741 |
| 1×150 | 3.4 | 2.0 | 1.5 | 1.4 | 40.9±2 | 3140 |
| 1×185 | 3.4 | 2.0 | 1.5 | 1.4 | 42.7±2 | 3612 |
| 1×240 | 3.4 | 2.2 | 1.6 | 1.6 | 46.3±2 | 4389 |
| 1×300 | 3.4 | 2.3 | 1.7 | 1.6 | 49.1±2 | 5177 |
| 1×400 | 3.4 | 2.4 | 1.7 | 1.6 | 52.2±2 | 6195 |
| 1×500 | 3.4 | 2.5 | 1.8 | 1.6 | 55.7±2 | 7424 |
| 1×630 | 3.4 | 2.7 | 1.9 | 1.6 | 60.2±2 | 9125 |
| 3×16 | 3.4 | 2.4 | 1.8 | 1.0 | 52.2±2 | 3969 |
| 3×25 | 3.4 | 2.5 | 1.8 | 1.2 | 55.6±2 | 4599 |
| 3×35 | 3.4 | 2.6 | 1.9 | 1.2 | 58.8±2 | 5292 |
| 3×50 | 3.4 | 2.7 | 2.0 | 1.2 | 61.7±2 | 6027 |
| 3×70 | 3.4 | 2.9 | 2.1 | 1.2 | 66.1±2 | 7245 |
| 3×95 | 3.4 | 3.1 | 2.2 | 1.4 | 71.2±2 | 8684 |
| 3×120 | 3.4 | 3.2 | 2.3 | 1.4 | 74.9±2 | 9944 |
| 3×150 | 3.4 | 3.3 | 2.4 | 1.4 | 78.8±2 | 11340 |
| 3×185 | 3.4 | 3.5 | 2.5 | 1.4 | 83.6±2 | 12989 |
| 3×240 | 3.4 | 3.7 | 2.7 | 1.6 | 91.4±2 | 15792 |
| 3×300 | 3.4 | 3.9 | 2.9 | 1.6 | 97.2±2 | 18323 |

NEK 606:2004

N

Standard

Zero

Halogen Free IEC60754-1

IEC 60092-351

N

Standard

Low Corrosivity IEC60754-2

IEC 60092-354

N

Standard

Low Smoke Emission IEC 61034-1&2

IEC 60092-359

N

Standard

Flame Retardancy IEC60332-1

Water Tightness VG 95218-29

Reduced Fire Propagation IEC60332-3-22

W	E

Circuit Integrity IEC 60331-21

www.caledonian-cables.co.uk

www.caledonian-cables.com 	47