NEK606	Water Blocked

Offshore & Marine Cables

Water Blocked P30 RFOU-HCF / TFOU-HCF 6/10(12) kV

Applications

These cables are partially water blocked, fire resistant, flame retardant, low smoke and halogen free, used for emergency control, power and lighting systems that need to be operational during a 1100˚C hydrocarbon fire.

Standards

	IEC 60092-354

	IEC 60092-351

	IEC 60092-359

	IEC 60331-21

	IEC 60332-1

	IEC 60332-3-22

	IEC 60754-1,2

	IEC 61034-1,2

	NEK 606:2004

- VG 95218 part 29

Construction

Polyurethane Outer Sheath 2 HC-fire Protection + Taping Water Blocking Tape Halogen-free Bedding Conductor Screen

Stranded Copper Conductor Insulation Screen

Water Blocking Fillers

HFEPR/XLPE Insulation Copper Wire Braid SHF2 Inner Sheath SHF1 Outer Sheath 1

- Conductors: Circular tinned annealed stranded copper to IEC 60228 class 2.

- Conductor Screen: Semi conducting material.

- Insulation: Halogen-free EPR. XLPE can be offered as an option.

- Insulation Screen: Semi conducting material and tinned copper wire braid.

- Filler: Water blocking fillers, if required.

- Bedding: Halogen free compound, PETP wrapping tape will be applied over the bedding, if required.

- Armour: Tinned copper wire braid, PETP wrapping tape will be applied over the

braiding, if required.

- Water Blocking Elements: Water blocking tape and strings for providing longitudinal

water tightness.

- Inner Sheath: Halogen free thermosetting compound, SHF2, coloured red.

- HC-fire protection: Extruded thermoplastic fire protection compound.

- Taping: Lapped glass fibre tape.

48

48	www.addison-tech.com

www.addison-cables.com

NEK606	Water Blocked

Offshore & Marine Cables

- Outer Sheath 1: Flame retardant halogen-free thermoplastic compound, SHF1,

coloured red.

- Outer Sheath 2: Polyurethane for providing transversal water tightness, PE is optional,but can not meet low smoke standard.

Optional

P31 RFOU-HCF / TFOU-HCF 8.7/15kV P32 RFOU-HCF / TFOU-HCF 12/20(24) kV P33 RFOU-HCF / TFOU-HCF 18/30(36) kV

Electrical Characteristics

| Nominal Cross Section Area | mm² | 70 | 95 | 120 | 150 | 185 | 240 | 300 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Nominal Conductor Diameter | mm | 10.3 | 12.2 | 13.8 | 15.1 | 17.0 | 19.6 | 21.9 |
| Maximum DC Resistant@20˚C | Ω/km | 0.27 | 0.195 | 0.154 | 0.126 | 0.1 | 0.0762 | 0.0607 |
| Continuous Current Rating@45˚C 1 Core | A | 242 | 293 | 339 | 389 | 444 | 522 | 601 |
| Continuous Current Rating@45˚C 3 Core | A | 169 | 205 | 237 | 272 | 311 | 365 | 421 |
| Short Circuit Current 1s | A | 10020 | 13590 | 17170 | 21460 | 26470 | 34340 | 42930 |
| Operating Voltage | KV | 6/10 | 6/10 | 6/10 | 6/10 | 6/10 | 6/10 | 6/10 |

Ambient Temperature Correction Factors

| Ambient Temperature Correction Factors | 35 | 40 | 45 | 50 | 55 | 60 | 65 | 70 | 75 | 80 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Rating Factor | 1.1 | 1.05 | 1.0 | 0.94 | 0.88 | 0.82 | 0.74 | 0.67 | 0.58 | 0.47 |

Mechanical and Thermal Properties

- Bending Radius: 20×OD (during installation); 12×OD (fixed installed)

- Temperature Range: -20˚C ~ +90˚C

Dimensions and Weight

www.caledonian-cables.co.uk

www.caledonian-cables.com 	49

NEK606	Water Blocked

Offshore & Marine Cables

| NEK 606:2004 Construction No. of cores×Cross section(mm²) | Nominal Insulation Thickness mm | Nominal Diameter Over Bedding mm | Nominal Diameter Over Inner Sheath mm | Nominal Overall Diameter mm | Nominal Weight kg/km |
| --- | --- | --- | --- | --- | --- |
| 1×70 | 3.4 | 23.5 | 30.0 | 64.4±2 | 5481 |
| 1×95 | 3.4 | 25.5 | 32.0 | 67.3±2 | 6195 |
| 1×120 | 3.4 | 27.5 | 34.0 | 69.3±2 | 6657 |
| 1×150 | 3.4 | 28.5 | 35.0 | 70.3±2 | 7004 |
| 1×185 | 3.4 | 30.5 | 36.5 | 71.8±2 | 7686 |
| 1×240 | 3.4 | 33.0 | 39.0 | 75.2±2 | 8663 |
| 1×300 | 3.4 | 35.0 | 41.5 | 77.7±2 | 9744 |
| 3×50 | 3.4 | 47.0 | 55.0 | 91.4±2 | 11519 |
| 3×95 | 3.4 | 54.0 | 62.5 | 99.8±2 | 14942 |
| 3×150 | 3.4 | 60.0 | 70.5 | 108.8±2 | 18270 |

N

Standard

Zero

Halogen Free IEC60754-1

IEC 60092-351

N

Standard

Low Corrosivity IEC60754-2

IEC 60092-354

N

Standard

Low Smoke Emission IEC 61034-1&2

IEC 60092-359

N

Standard

Flame Retardancy IEC60332-1

Water Tightness VG 95218-29

Reduced Fire Propagation IEC60332-3-22

W	E

Circuit Integrity IEC 60331-21

50	www.addison-tech.com

www.addison-cables.com