NEK606	Water Blocked

Offshore & Marine Cables

Water Blocked S14 BU(c) 250 V

Applications

These unarmoured cables are partially water blocked, fire resistant, flame retardant, low smoke and halogen free, used for instrumentation, communication, control and alarm systems.

Standards

	IEC 60092-376

	IEC 60092-351

	IEC 60092-359

	IEC 60331-21

	IEC 60332-1

	IEC 60332-3-22

	IEC 60754-1,2

	IEC 61034-1,2

	NEK 606:2004

- VG 95218 part 29

Construction

SHF2 Inner Sheath Copper/Polyester Tape + Drain Wire Water Blocking Fillers

Mica Tape + HFEPR Insulation Stranded Copper Conductor Water Blocking tape Polyurethane Outer Sheath

- Conductors: Circular tinned annealed stranded copper wire to IEC 60228 class 2.

- Insulation: Mica tape + Halogen free EPR compound.

- Twinning: Colour coded cores twisted together.

- Collective Shielding: Pairs/triples are layed up and collectively screened by copper backed polyester tape in contact with a stranded tinned copper drain wire. Pairs/triples are numbered with numbered tape or by numbers printed directly on the insulated conductors.

- Filler: Water blocking fillers, if required.

- Water Blocking Elements: Water blocking tape and strings for providing longitudinal

water tightness.

- Inner Sheath: Halogen free thermosetting compound, SHF2, coloured grey (blue for intrinsically safe).

- Outer Sheath: Polyurethane for providing transversal water tightness, PE is optional,but can not meet low smoke standard.

92	www.addison-tech.com

www.addison-cables.com

NEK606	Water Blocked

Offshore & Marine Cables

Electrical Characteristics

| Nominal Cross Section Area | mm² | 0.75 | 1.0 | 1.5 |
| --- | --- | --- | --- | --- |
| Nominal Conductor Diameter | mm | 1.1 | 1.3 | 1.6 |
| Maximum Resistant@20˚C | Ω/km | 26.3 | 19.3 | 12.9 |
| Mutual Capacitance | nF/km | 75 | 80 | 85 |
| Nominal Inductance@1KHz | MH/km | 0.727 | 0.686 | 0.667 |
| Maximum L/R@1KHz | μH/Ω | 20 | 25 | 35 |
| Operating Voltage | V | 250 | 250 | 250 |

Mechanical and Thermal Properties

- Bending Radius: 8×OD (during installation); 6×OD (fixed installed)

- Temperature Range: -20˚C ~ +90˚C

Dimensions and Weight

| Construction No. of elements×No. of cores in element×Cross section(mm²) | Nominal Insulation Thickness mm | Nominal Inner Sheath Thickness mm | Nominal Outer Sheath Thickness mm | Nominal Overall Diameter mm | Nominal Weight kg/km |
| --- | --- | --- | --- | --- | --- |
| 2×2×0.75 | 0.6 | 1.1 | 1.0 | 12.2±2 | 194 |
| 4×2×0.75 | 0.6 | 1.2 | 1.0 | 14.5±2 | 252 |
| 7×2×0.75 | 0.6 | 1.4 | 1.0 | 17.0±2 | 368 |
| 8×2×0.75 | 0.6 | 1.4 | 1.0 | 18.3±2 | 415 |
| 12×2×0.75 | 0.6 | 1.5 | 1.0 | 21.5±2 | 567 |
| 16×2×0.75 | 0.6 | 1.6 | 1.0 | 23.8±2 | 725 |
| 19×2×0.75 | 0.6 | 1.7 | 1.0 | 25.2±2 | 819 |
| 24×2×0.75 | 0.6 | 1.8 | 1.0 | 28.7±2 | 1034 |
| 32×2×0.75 | 0.6 | 2.1 | 1.0 | 31.6±2 | 1286 |
| 2×3×0.75 | 0.6 | 1.2 | 1.0 | 14.0±2 | 215 |
| 3×3×0.75 | 0.6 | 1.2 | 1.0 | 15.1±2 | 278 |
| 4×3×0.75 | 0.6 | 1.3 | 1.0 | 16.4±2 | 336 |
| 7×3×0.75 | 0.6 | 1.3 | 1.0 | 19.4±2 | 499 |
| 8×3×0.75 | 0.6 | 1.5 | 1.0 | 21.5±2 | 620 |
| 12×3×0.75 | 0.6 | 1.6 | 1.0 | 24.9±2 | 782 |
| 16×3×0.75 | 0.6 | 1.7 | 1.0 | 27.6±2 | 1013 |
| 19×3×0.75 | 0.6 | 1.8 | 1.0 | 29.2±2 | 1150 |
| 24×3×0.75 | 0.6 | 2.0 | 1.0 | 33.6±2 | 1475 |
| 2×2×1.0 | 0.6 | 1.1 | 1.0 | 12.7±2 | 221 |
| 4×2×1.0 | 0.6 | 1.1 | 1.0 | 15.3±2 | 299 |
| 7×2×1.0 | 0.6 | 1.4 | 1.0 | 18.0±2 | 436 |
| 8×2×1.0 | 0.6 | 1.4 | 1.0 | 19.3±2 | 488 |

www.caledonian-cables.co.uk

www.caledonian-cables.com 	93

NEK606	Water Blocked

Offshore & Marine Cables

| NEK 606:2004 Construction No. of elements×No. of cores in element×Cross section(mm²) | Nominal Insulation Thickness mm | Nominal Inner Sheath Thickness mm | Nominal Outer Sheath Thickness mm | Nominal Overall Diameter mm | Nominal Weight kg/km |
| --- | --- | --- | --- | --- | --- |
| 12×2×1.0 | 0.6 | 1.6 | 1.0 | 22.8±2 | 677 |
| 16×2×1.0 | 0.6 | 1.7 | 1.0 | 25.3±2 | 866 |
| 19×2×1.0 | 0.6 | 1.8 | 1.0 | 26.7±2 | 987 |
| 24×2×1.0 | 0.6 | 1.9 | 1.0 | 30.8±2 | 1260 |
| 32×2×1.0 | 0.6 | 2.3 | 1.0 | 33.8±2 | 1570 |
| 3×3×1.0 | 0.6 | 1.2 | 1.0 | 16.0±2 | 326 |
| 4×3×1.0 | 0.6 | 1.4 | 1.0 | 17.3±2 | 399 |
| 7×3×1.0 | 0.6 | 1.6 | 1.0 | 20.6±2 | 599 |
| 12×3×1.0 | 0.6 | 1.6 | 1.0 | 26.4±2 | 945 |
| 16×3×1.0 | 0.6 | 1.7 | 1.0 | 29.3±2 | 1218 |
| 19×3×1.0 | 0.6 | 1.9 | 1.0 | 31.0±2 | 1391 |
| 24×3×1.0 | 0.6 | 2.1 | 1.0 | 35.7±2 | 1785 |
| 2×2×1.5 | 0.7 | 1.2 | 1.0 | 14.1±2 | 289 |
| 4×2×1.5 | 0.7 | 1.3 | 1.0 | 17.2±2 | 399 |
| 7×2×1.5 | 0.7 | 1.5 | 1.0 | 20.4±2 | 593 |
| 8×2×1.5 | 0.7 | 1.5 | 1.0 | 22.0±2 | 672 |
| 12×2×1.5 | 0.7 | 1.7 | 1.0 | 26.3±2 | 940 |
| 16×2×1.5 | 0.7 | 1.8 | 1.0 | 29.2±2 | 1208 |
| 19×2×1.5 | 0.7 | 1.9 | 1.0 | 30.6±2 | 1360 |
| 24×2×1.5 | 0.7 | 2.1 | 1.0 | 35.5±2 | 1754 |
| 32×2×1.5 | 0.7 | 2.3 | 1.0 | 39.0±2 | 2200 |
| 2×3×1.5 | 0.7 | 1.3 | 1.0 | 17.0±2 | 326 |
| 3×3×1.5 | 0.7 | 1.3 | 1.0 | 18.0±2 | 441 |
| 4×3×1.5 | 0.7 | 1.4 | 1.0 | 19.7±2 | 541 |
| 7×3×1.5 | 0.7 | 1.6 | 1.0 | 23.5±2 | 824 |
| 8×3×1.5 | 0.7 | 1.6 | 1.0 | 25.5±2 | 977 |
| 12×3×1.5 | 0.7 | 1.8 | 1.0 | 30.5±2 | 1318 |
| 16×3×1.5 | 0.7 | 1.9 | 1.0 | 33.9±2 | 1712 |
| 19×3×1.5 | 0.7 | 2.0 | 1.0 | 35.8±2 | 1948 |
| 24×3×1.5 | 0.7 | 2.2 | 1.0 | 41.3±2 | 2494 |

N

Standard

Zero

Halogen Free IEC60754-1

IEC 60092-351

N

Standard

Low Corrosivity IEC60754-2

IEC 60092-376

N

Standard

Low Smoke Emission IEC 61034-1&2

IEC 60092-359

N

Standard

Flame Retardancy IEC60332-1

Water Tightness VG 95218-29

Reduced Fire Propagation IEC60332-3-22

W	E

Circuit Integrity IEC 60331-21

94	www.addison-tech.com

www.addison-cables.com