NEK606	Water Blocked

Offshore & Marine Cables

Water Blocked S15 BFOU-HCF(i) 250 V

Applications

These cables are partially water blocked, fire resistant, flame retardant, low smoke and halogen free, used for emergency instrumentation, communication, control and alarm systems that need to be operational during a 1100˚C hydrocarbon fire.

Standards

	IEC 60092-376

	IEC 60092-351

	IEC 60092-359

	IEC 60331-21

	IEC 60332-1

	IEC 60332-3-22

	IEC 60754-1,2

	IEC 61034-1,2

	NEK 606:2004

- VG 95218 part 29

Construction

SHF1 Outer Sheath 1

HC-fire Protection Compound Water Blocking tape

Conductor + Mica Tape + HFEPR Insulation Halogen-free Bedding

Copper/polyester Tape + Drain Wire

Water Blocking Fillers Copper Wire Braid SHF2 Inner Sheath Glass Fiber Taping

Polyurethane Outer Sheath 2

- Conductors: Circular tinned annealed stranded copper wire to IEC 60228 class 2.

- Insulation: Mica tape + Halogen free EPR compound.

- Twinning: Colour coded cores twisted together.

- Individual Shielding: Each pairs/triples are screened by copper backed polyester tape in contact with a stranded tinned copper drain wire and wrapped with polyester tape. Pairs/triples are numbered with numbered tape or by numbers printed directly on the insulated conductors.

- Filler: Water blocking fillers, if required.

- Bedding: Halogen free compound, PETP wrapping tape will be applied over the bedding, if required.

- Armour: Tinned copper wire braid, PETP wrapping tape will be applied over the

braiding, if required.

- Water Blocking Elements: Water blocking tape and strings for providing longitudinal

water tightness.

www.caledonian-cables.co.uk

www.caledonian-cables.com 	95

NEK606	Water Blocked

Offshore & Marine Cables

- Inner Sheath: Halogen free thermosetting compound, SHF2.

- HC-fire protection: Extruded thermoplastic fire protection compound.

- Taping: Lapped glass fibre tape.

- Outer Sheath 1: Flame retardant halogen-free thermoplastic compound, type SHF1, coloured grey (blue for intrinsically safe).

- Outer Sheath 2: Polyurethane for providing transversal water tightness, PE is optional,but can not meet low smoke standard.

Electrical Characteristics

| Nominal Cross Section Area | mm² | 1.5 |
| --- | --- | --- |
| Nominal Conductor Diameter | mm | 1.6 |
| Maximum Resistant@20˚C | Ω/km | 12.9 |
| Mutual Capacitance | nF/km | 100 |
| Nominal Inductance@1KHz | MH/km | 0.673 |
| Operating Voltage | V | 250 |

Mechanical and Thermal Properties

- Bending Radius: 20×OD (during installation); 12×OD (fixed installed)

- Temperature Range: -20˚C ~ +90˚C

96	www.addison-tech.com

www.addison-cables.com

NEK606	Water Blocked

Offshore & Marine Cables

Dimensions and Weight

| Construction No. of elements×No. of cores in element×Cross section(mm²) | Nominal Insulation Thickness mm | Nominal Diameter Over Bedding mm | Nominal Diameter Over Inner Sheath mm | Nominal Overall Diameter mm | Nominal Weight kg/km |
| --- | --- | --- | --- | --- | --- |
| 1×2×1.5 | 0.7 | 9.0 | 13.1 | 41.5±2 | 1974 |
| 2×2×1.5 | 0.7 | 13.0 | 16.8 | 46.5±2 | 2573 |
| 4×2×1.5 | 0.7 | 15.0 | 20.7 | 49.5±2 | 2972 |
| 8×2×1.5 | 0.7 | 21.0 | 26.4 | 56.0±2 | 3875 |
| 12×2×1.5 | 0.7 | 25.0 | 31.2 | 65.0±2 | 5460 |

NEK 606:2004

N

Standard

Zero

Halogen Free IEC60754-1

IEC 60092-351

N

Standard

Low Corrosivity IEC60754-2

IEC 60092-376

N

Standard

Low Smoke Emission IEC 61034-1&2

IEC 60092-359

N

Standard

Flame Retardancy IEC60332-1

Water Tightness VG 95218-29

Reduced Fire Propagation IEC60332-3-22

W	E

Circuit Integrity IEC 60331-21

www.caledonian-cables.co.uk

www.caledonian-cables.com 	97