Caledonian

Fire Resistant Fire Alarm Cables

www.caledonian-tech.net	www.caledonian-tech.com

300/500V SR Insulated & LSZH Sheathed Fire Alarm Cables

FFX200P 05SOZ1-U (PH30) (CU/SR/OSCR/LSZH 300/500V Class 1)

FFX200P 05SOZ1-R (PH30) (CU/SR/OSCR/LSZH 300/500V Class 2)

APPLICATION

The cables are designed, manufactured and tested as data transmission cables for emergency services. These are primarily intended for for indoor instrumentation and control cabling, electrically noisy environments and fire alarm systems in office buildings when high frequency signal transmission has to be assured in the event of a fire.

STANDARDS

Basic design to BS 7629-1

Fire Performance

|  | IEC 60331-21; BS 6387 CWZ; DIN VDE 0472-814(FE180); |  |
| --- | --- | --- |
| Circuit Integrity | BS 8434-1 (30mins); BS 5839-1 Clause 26 2d; CEI 20-36/2-1; |  |
|  | SS229-1; NBN C 30-004 (cat. F3); NF C32-070-2.3(CR1) |  |
| Circuit Integrity with mechanical | EN 50200(PH30); CEI 20-36/4-0 |  |
| shock |  |  |
| Circuit Integrity with mechanical | EN 50200 annex E |  |
| shock & water spray |  |  |
| System circuit integrity | DIN 4102-12, E30 depending on lay system |  |

Flame Retardance (Single Vertical EN 60332-1-2; IEC 60332-1-2; BS EN 60332-1-2;

Wire Test) VDE 0482-332-1 ; NBN C 30-004 (cat. F1); NF C32-070-2.1(C2); CEI 20-35/1-2; EN 50265-2-1*; DIN VDE 0482-265-2-1*

| Reduced Fire Propagation | EN 60332-3-24 (cat. C); IEC 60332-3-24; BS EN 60332-3-24; |  |
| --- | --- | --- |
| (Vertically-mounted bundled wires VDE 0482-332-3; NBN C 30-004 (cat. F2); NF C32-070-2.2(C1); |  |  |
| & cable test) | CEI 20-22/3-4; EN 50266-2-4*; DIN VDE 0482-266-2-4 |  |
| Halogen Free | IEC 60754-1; EN 50267-2-1; DIN VDE 0482-267-2-1; |  |
|  | CEI 20-37/2-1 ; BS 6425-1* |  |
| No Corrosive Gas Emission | IEC 60754-2; EN 50267-2-2; DIN VDE 0482-267-2-2; |  |
|  | CEI 20-37/2-2 ; BS 6425-2* |  |

ADDISON   103

ADDISON

| Minimum Smoke Emission | IEC 61034-1&2; EN 61034 -1&2; DIN VDE 0482-1034-1&2; |  |
| --- | --- | --- |
|  | CEI 20-37/3-1&2; EN 50268-1&2*; BS 7622-1&2* |  |
| No Toxic gases | NES 02-713; NF C 20-454 |  |

Note: Asterisk * denotes superseded standard.

CABLE CONSTRUCTION

Conductors: Plain annealed copper wire, solid according to IEC(EN) 60228 class 1, stranded according to IEC(EN) 60228 class 2.

Insulation: Fire resistant silicone rubber compound type EI2 as per BS 7655-1.1.

Cabling Elements: Insulated cores are twisted to form pairs with varying lay length to minimize crosstalk. Two-pair cable had four cores laid in quad formation.

Cabling: Pairs are cabled together in concentric layers with suitable non-hygroscopic fillers.

Overall screen: Aluminum/polyester tape with tinned copper drain wire.

Outer Sheath: Thermoplastic LSZH compound type LTS3 as per BS 7655-6.1 (Thermosetting LSZH compound type SW2-SW4 as per BS 7655-2.6 can be offered.)

Colour code

Insulation Colour:

Cables up to 6 pairs black-red / black-blue / red-blue / yellow-black /yellow-red / yellow-blue Cables above 6 pairs all pairs black-red numbered on the wrapping tape.

Sheath Colour: Colour red (other colours on request).

Physical AND THERMAL PROPERTIES

Temperature range during operation (fixed state):-30°C – +90°C

Temperature range during installation (mobile state): -20°C – +50°C

Minimum bending radius: 7.5 x Overall Diameter

CONSTRUCTION PARAMETERS

|  | Nominal | Nominal | Nominal | Approx. |  |
| --- | --- | --- | --- | --- | --- |
| Cable Code | Insulation | Sheath | Overall |  |  |
|  |  |  |  | Weight |  |
|  | Thickness | Thickness | Diameter |  |  |
| mm2 | mm | mm | mm | kg/km |  |
| 1 Pairs |  |  |  |  |  |
| 1x2x1 stranded FFX200P 05SOZ1-R (PH30) | 0.6 | 0.9 | 7.4 | 77 |  |
| 1x2x1.5 stranded FFX200P 05SOZ1-R (PH30) | 0.7 | 0.9 | 8,7 | 100 |  |
| 2 Pairs |  |  |  |  |  |
| 2x2x1 stranded FFX200P 05SOZ1-R (PH30) | 0.6 | 1.0 | 10.6 | 130 |  |
| 2x2x1.5 stranded FFX200P 05SOZ1-R (PH30) | 0.7 | 1.0 | 10.2 | 188 |  |
| 3 Pairs |  |  |  |  |  |
| 3x2x1 stranded FFX200P 05SOZ1-R (PH30) | 0.6 | 1.1 | 11.2 | 196 |  |

104	Caledonian   sales@caledonian-cables.net   uk@caledonian-cables.net

Caledonian

Fire Resistant Fire Alarm Cables

www.caledonian-tech.net	www.caledonian-tech.com

| 3x2x1.5 stranded FFX200P 05SOZ1-R (PH30) | 0.7 | 1.1 | 12.9 | 223 |
| --- | --- | --- | --- | --- |
| 5 Pairs |  |  |  |  |
| 5x2x1 stranded FFX200P 05SOZ1-R (PH30) | 0.6 | 1.2 | 13.7 | 245 |
| 5x2x1.5 stranded FFX200P 05SOZ1-R (PH30) | 0.7 | 1.3 | 16.7 | 346 |
| 6 Pairs |  |  |  |  |
| 6x2x1 stranded FFX200P 05SOZ1-R (PH30) | 0.6 | 1.2 | 14.8 | 300 |
| 6x2x1.5 stranded FFX200P 05SOZ1-R (PH30) | 0.7 | 1.3 | 17.5 | 426 |
| 10 Pairs |  |  |  |  |
| 10x2x1 stranded FFX200P 05SOZ1-R (PH30) | 0.6 | 1.4 | 18.9 | 378 |
| 10x2x1.5 stranded FFX200P 05SOZ1-R (PH30) | 0.7 | 1.5 | 23.4 | 541 |
| 15 Pairs |  |  |  |  |
| 15x2x1 stranded FFX200P 05SOZ1-R (PH30) | 0.6 | 1.5 | 23.2 | 567 |
| 15x2x1.5 stranded FFX200P 05SOZ1-R (PH30) | 0.7 | 1.6 | 28.9 | 892 |
| 20 Pairs |  |  |  |  |
| 20x2x1 stranded FFX200P 05SOZ1-R (PH30) | 0.6 | 1.6 | 26.2 | 831 |
| 20x2x1.5stranded FFX200P 05SOZ1-R (PH30) | 0.7 | 1.8 | 32.5 | 1182 |

approximate values

| 300/500V | BS 7629-1 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | W | E |  |  |  |
|  | N IECCircuit60331/BSIntegrity6387 |  |  | Reduced Fire Propagation | Flame Retardancy |  |
|  |  |  | EN 50200 | NF C32-070-2.2(C1) | NF C32-070-2.1(C2) |  |
| Rated Voltage |  | NF C32-070-2.3(CR1) |  |  |  |  |
|  | Standard |  |  | IEC60332-3-24/EN50266-2-4 | IEC60332-1-2/EN50265-2-1 |  |

Zero

W

E

|  | Low Corrosivity | Low Smoke Emission | Halogen Free |  |  |
| --- | --- | --- | --- | --- | --- |
| Low Toxicity | IEC60754-2 |  |  |  |  |
|  |  | IEC 61034-1&2 | IEC60754-1 |  |  |
| NES 02-713/NF C 20-454 | EN50267-2-2/3 |  |  | Functional Integrity |  |
|  | NF C 32-074 | EN 50268-1&2/NF C32-073 | EN50267-2-1 | DIN 4102-12 |  |

ADDISON   105