Water Blocked P5 or P5/P12 BFOU 0.6/1KV

Applications

These cables are partially water blocked, fire resistant, flame retardant, low smoke, halogen free and mud resistant, used for control, power and lighting systems.

Standards

	IEC 60092-353

	IEC 60092-351

	IEC 60092-359

	IEC 60331-21

	IEC 60332-1

	IEC 60332-3-22

	IEC 60754-1,2

	IEC 61034-1,2

	NEK 606:2004

- VG 95218 part 29

Construction

SHF2/SHF MUD Inner Sheath Copper Wire Braid

Water Blocking Fillers

Stranded Copper Conductor

Mica Tape + HFEPR/XLPE Insulation Halogen-free Bedding

Water Blocking tape

Polyurethane Outer Sheath

- Conductors: Tinned annealed stranded compacted copper to IEC 60228 class 2.

- Insulation: Mica tape + Halogen free EPR/Mica tape + XLPE.

- Filler: Water blocking fillers, if required.

- Bedding: Halogen free compound, PETP wrapping tape will be applied over the bedding, if required.

- Armour: Tinned copper wire braid, PETP wrapping tape will be applied over the

braiding, if required.

- Water Blocking Elements: Water blocking tape and strings for providing longitudinal

water tightness.

- Inner Sheath: Halogen free thermosetting compound, SHF2 (for TYPE P5). Halogen free, mud resistant thermosetting compound, SHF MUD (for TYPE P5/P12), coloured black.

- Outer Sheath: Polyurethane for providing transversal water tightness, PE is optional,but can not meet low smoke standard.

Electrical Characteristics

| Nominal Cross Section Area | mm² | 1.5 | 2.5 | 4 | 6 | 10 | 16 | 25 | 35 | 50 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Nominal Conductor Diameter | mm | 1.6 | 2.1 | 2.6 | 3.2 | 4 | 5.1 | 6.5 | 7.4 | 8.7 |
| Maximum DC Resistant@20˚C | Ω/km | 12.2 | 7.56 | 4.7 | 3.11 | 1.84 | 1.16 | 0.734 | 0.529 | 0.391 |
| Continuous Current Rating@45˚C 1 Core | A | 23 | 30 | 40 | 52 | 72 | 96 | 127 | 157 | 196 |
| Continuous Current Rating@45˚C 2 Core | A | 20 | 26 | 34 | 44 | 61 | 82 | 108 | 133 | 167 |
| Continuous Current Rating@45˚C 3&4 Core | A | 16 | 21 | 28 | 36 | 50 | 67 | 89 | 110 | 137 |
| Short Circuit Current 1s | A | 210 | 360 | 570 | 860 | 1430 | 2290 | 3580 | 5010 | 7150 |
| Operating Voltage | KV | 0.6/1 | 0.6/1 | 0.6/1 | 0.6/1 | 0.6/1 | 0.6/1 | 0.6/1 | 0.6/1 | 0.6/1 |
| Nominal Cross Section Area | mm² | 70 | 95 | 120 | 150 | 185 | 240 | 300 | 400 | 630 |
| Nominal Conductor Diameter | mm | 10.3 | 12.2 | 13.8 | 15.1 | 17.0 | 19.6 | 21.9 | 24.6 | 32.5 |
| Maximum DC Resistant@20˚C | Ω/km | 0.27 | 0.195 | 0.154 | 0.126 | 0.1 | 0.0762 | 0.0607 | 0.0475 | 0.0286 |
| Continuous Current Rating@45˚C 1 Core | A | 242 | 293 | 339 | 389 | 444 | 522 | 601 | 690 | 890 |
| Continuous Current Rating@45˚C 2 Core | A | 206 | 249 | 288 | 331 | 444 | 444 | 511 | 587 | 757 |
| Continuous Current Rating@45˚C 3&4 Core | A | 169 | 205 | 237 | 272 | 311 | 365 | 421 | 483 | 623 |
| Short Circuit Current 1s | A | 10020 | 13590 | 17170 | 21460 | 26470 | 34340 | 42930 | 57230 | 90140 |
| Operating Voltage | KV | 0.6/1 | 0.6/1 | 0.6/1 | 0.6/1 | 0.6/1 | 0.6/1 | 0.6/1 | 0.6/1 | 0.6/1 |

Note: For more than 4-cores, the current ratings may be calculated from the following

formula (IN = I1 / 3

N ), I1= Current rating for 1-core, N = Number of cores.

Ambient Temperature Correction Factors

| Ambient Temperature Correction Factors | 35 | 40 | 45 | 50 | 55 | 60 | 65 | 70 | 75 | 80 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Rating Factor | 1.1 | 1.05 | 1.0 | 0.94 | 0.88 | 0.82 | 0.74 | 0.67 | 0.58 | 0.47 |

Mechanical and Thermal Properties

- Bending Radius: 8×OD (during installation); 6×OD (fixed installed)

- Temperature Range: -20˚C ~ +90˚C

Dimensions and Weight

| Construction No. of cores×Cross section(mm²) | Nominal Insulation Thickness mm | Nominal Bedding Thickness mm | Nominal Inner Sheath Thickness mm | Nominal Outer Sheath Thickness mm | Nominal Overall Diameter mm | Nominal Weight kg/km |
| --- | --- | --- | --- | --- | --- | --- |
| 1×1.5 | 1.0 | 1.1 | 1.1 | 1.0 | 11.3±2 | 152 |
| 1×2.5 | 1.0 | 1.1 | 1.1 | 1.0 | 11.7±2 | 168 |
| 1×4 | 1.0 | 1.1 | 1.1 | 1.0 | 12.4±2 | 231 |
| 1×6 | 1.0 | 1.1 | 1.1 | 1.0 | 12.9±2 | 263 |
| 1×10 | 1.0 | 1.1 | 1.2 | 1.0 | 14.7±2 | 326 |
| 1×16 | 1.0 | 1.1 | 1.2 | 1.0 | 15.9±2 | 410 |
| 1×25 | 1.2 | 1.1 | 1.3 | 1.2 | 18.7±2 | 614 |
| 1×35 | 1.2 | 1.1 | 1.3 | 1.2 | 19.6±2 | 725 |
| 1×50 | 1.4 | 1.1 | 1.4 | 1.2 | 21.4±2 | 935 |
| 1×70 | 1.4 | 1.1 | 1.4 | 1.2 | 23.0±2 | 1166 |
| 1×95 | 1.6 | 1.1 | 1.5 | 1.4 | 25.9±2 | 1512 |
| 1×120 | 1.6 | 1.2 | 1.6 | 1.4 | 27.8±2 | 1822 |
| 1×150 | 1.8 | 1.2 | 1.7 | 1.4 | 29.8±2 | 2163 |
| 1×185 | 2.0 | 1.2 | 1.7 | 1.4 | 32.2±2 | 2672 |
| 1×240 | 2.2 | 1.2 | 1.8 | 1.6 | 35.8±2 | 3329 |
| 1×300 | 2.4 | 1.2 | 1.9 | 1.6 | 38.5±2 | 4106 |
| 1×400 | 2.4 | 1.4 | 2.1 | 1.6 | 44.2±2 | 5355 |
| 1×630 | 2.8 | 1.4 | 2.3 | 1.6 | 51.7±2 | 8043 |
| 2×1.5 | 1.0 | 1.1 | 1.2 | 1.0 | 16.2±2 | 326 |
| 2×2.5 | 1.0 | 1.1 | 1.3 | 1.0 | 17.1±2 | 378 |
| 2×4 | 1.0 | 1.1 | 1.3 | 1.0 | 18.6±2 | 494 |
| 2×6 | 1.0 | 1.1 | 1.4 | 1.0 | 19.9±2 | 583 |
| 2×10 | 1.0 | 1.1 | 1.4 | 1.0 | 21.9±2 | 740 |
| 2×16 | 1.0 | 1.1 | 1.5 | 1.0 | 24.5±2 | 1034 |
| 2×25 | 1.2 | 1.2 | 1.6 | 1.2 | 28.8±2 | 1428 |
| 2×35 | 1.2 | 1.2 | 1.7 | 1.2 | 30.8±2 | 1701 |
| 2×50 | 1.4 | 1.2 | 1.9 | 1.2 | 34.8±2 | 2405 |
| 2×70 | 1.4 | 1.2 | 2.1 | 1.2 | 40.4±2 | 3423 |
| 2×95 | 1.6 | 1.2 | 2.3 | 1.4 | 44.4±2 | 4106 |
| 2×120 | 1.6 | 1.4 | 2.4 | 1.4 | 48.1±2 | 4946 |
| 2×150 | 1.8 | 1.4 | 2.6 | 1.4 | 52.5±2 | 5954 |
| 2×185 | 2.0 | 1.4 | 2.7 | 1.4 | 57.1±2 | 7182 |
| 2×240 | 2.2 | 1.6 | 3.0 | 1.6 | 64.7±2 | 9230 |
| 2×300 | 2.4 | 1.6 | 3.2 | 1.6 | 71.0±2 | 11162 |
| 3×1.5 | 1.0 | 1.1 | 1.3 | 1.0 | 16.8±2 | 362 |
| 3×2.5 | 1.0 | 1.1 | 1.3 | 1.0 | 18.2±2 | 467 |
| 3×4 | 1.0 | 1.1 | 1.3 | 1.0 | 19.4±2 | 557 |

| Construction No. of cores×Cross section(mm²) | Nominal Insulation Thickness mm | Nominal Bedding Thickness mm | Nominal Inner Sheath Thickness mm | Nominal Outer Sheath Thickness mm | Nominal Overall Diameter mm | Nominal Weight kg/km |
| --- | --- | --- | --- | --- | --- | --- |
| 3×6 | 1.0 | 1.1 | 1.4 | 1.0 | 20.7±2 | 667 |
| 3×10 | 1.0 | 1.1 | 1.5 | 1.0 | 23.1±2 | 872 |
| 3×16 | 1.0 | 1.1 | 1.5 | 1.0 | 25.7±2 | 1218 |
| 3×25 | 1.2 | 1.2 | 1.7 | 1.2 | 30.5±2 | 1722 |
| 3×35 | 1.2 | 1.2 | 1.8 | 1.2 | 32.6±2 | 2079 |
| 3×50 | 1.4 | 1.2 | 2.0 | 1.2 | 36.7±2 | 2888 |
| 3×70 | 1.4 | 1.2 | 2.2 | 1.2 | 41.4±2 | 3859 |
| 3×95 | 1.6 | 1.4 | 2.4 | 1.4 | 47.5±2 | 5203 |
| 3×120 | 1.6 | 1.4 | 2.5 | 1.4 | 51.1±2 | 6337 |
| 3×150 | 1.8 | 1.4 | 2.7 | 1.4 | 56.0±2 | 7723 |
| 3×185 | 2.0 | 1.6 | 2.9 | 1.4 | 62.3±2 | 9476 |
| 3×240 | 2.2 | 1.6 | 3.2 | 1.6 | 69.7±2 | 12170 |
| 3×300 | 2.4 | 1.8 | 3.4 | 1.6 | 75.8±2 | 14427 |
| 4×1.5 | 1.0 | 1.1 | 1.3 | 1.0 | 18.4±2 | 420 |
| 4×2.5 | 1.0 | 1.1 | 1.3 | 1.0 | 19.3±2 | 530 |
| 4×4 | 1.0 | 1.1 | 1.4 | 1.0 | 20.8±2 | 651 |
| 4×6 | 1.0 | 1.1 | 1.4 | 1.0 | 22.1±2 | 788 |
| 4×10 | 1.0 | 1.1 | 1.5 | 1.0 | 24.7±2 | 1034 |
| 4×16 | 1.0 | 1.2 | 1.6 | 1.0 | 27.9±2 | 1470 |
| 4×25 | 1.2 | 1.2 | 1.8 | 1.2 | 33.1±2 | 2095 |
| 4×35 | 1.2 | 1.2 | 1.9 | 1.2 | 35.5±2 | 2562 |
| 4×50 | 1.4 | 1.4 | 2.0 | 1.2 | 40.6±2 | 3602 |
| 4×70 | 1.4 | 1.4 | 2.2 | 1.2 | 45.1±2 | 4830 |
| 4×95 | 1.6 | 1.6 | 2.4 | 1.4 | 52.2±2 | 6442 |
| 4×120 | 1.6 | 1.6 | 2.5 | 1.4 | 56.4±2 | 7891 |
| 4×150 | 1.8 | 1.6 | 2.9 | 1.4 | 61.8±2 | 9461 |
| 4×185 | 2.0 | 1.6 | 3.1 | 1.4 | 67.5±2 | 11550 |
| 4×240 | 2.2 | 1.8 | 3.4 | 1.6 | 76.3±2 | 14868 |
| 4×300 | 2.4 | 1.8 | 3.7 | 1.6 | 83.9±2 | 18428 |
| 5×1.5 | 1.0 | 1.1 | 1.4 | 1.0 | 19.7±2 | 536 |
| 6×1.5 | 1.0 | 1.1 | 1.4 | 1.0 | 21.0±2 | 572 |
| 7×1.5 | 1.0 | 1.1 | 1.4 | 1.0 | 21.0±2 | 620 |
| 8×1.5 | 1.0 | 1.1 | 1.5 | 1.0 | 23.8±2 | 751 |
| 9×1.5 | 1.0 | 1.1 | 1.6 | 1.0 | 25.3±2 | 756 |
| 10×1.5 | 1.0 | 1.1 | 1.6 | 1.0 | 25.6±2 | 830 |
| 12×1.5 | 1.0 | 1.2 | 1.6 | 1.0 | 26.3±2 | 924 |
| 14×1.5 | 1.0 | 1.2 | 1.7 | 1.0 | 27.5±2 | 1013 |
| 16×1.5 | 1.0 | 1.2 | 1.7 | 1.0 | 28.7±2 | 1087 |
| 19×1.5 | 1.0 | 1.2 | 1.7 | 1.0 | 29.4±2 | 1244 |
| 20×1.5 | 1.0 | 1.2 | 1.8 | 1.0 | 31.5±2 | 1323 |

| Construction No. of cores×Cross section(mm²) | Nominal Insulation Thickness mm | Nominal Bedding Thickness mm | Nominal Inner Sheath Thickness mm | Nominal Outer Sheath Thickness mm | Nominal Overall Diameter mm | Nominal Weight kg/km |
| --- | --- | --- | --- | --- | --- | --- |
| 23×1.5 | 1.0 | 1.2 | 1.9 | 1.0 | 33.8±2 | 1507 |
| 24×1.5 | 1.0 | 1.2 | 2.0 | 1.0 | 35.2±2 | 1586 |
| 27×1.5 | 1.0 | 1.2 | 2.0 | 1.0 | 35.9±2 | 1696 |
| 30×1.5 | 1.0 | 1.2 | 2.0 | 1.0 | 36.9±2 | 1822 |
| 32×1.5 | 1.0 | 1.4 | 2.0 | 1.0 | 37.5±2 | 1890 |
| 33×1.5 | 1.0 | 1.4 | 2.0 | 1.0 | 38.7±2 | 2037 |
| 37×1.5 | 1.0 | 1.4 | 2.0 | 1.0 | 40.0±2 | 2195 |
| 44×1.5 | 1.0 | 1.4 | 2.3 | 1.0 | 44.6±2 | 2583 |
| 5×2.5 | 1.0 | 1.1 | 1.4 | 1.0 | 20.8±2 | 625 |
| 6×2.5 | 1.0 | 1.1 | 1.4 | 1.0 | 22.4±2 | 683 |
| 7×2.5 | 1.0 | 1.1 | 1.4 | 1.0 | 22.4±2 | 735 |
| 8×2.5 | 1.0 | 1.1 | 1.5 | 1.0 | 25.5±2 | 830 |
| 9×2.5 | 1.0 | 1.1 | 1.6 | 1.0 | 27.1±2 | 903 |
| 10×2.5 | 1.0 | 1.1 | 1.6 | 1.0 | 27.4±2 | 1003 |
| 12×2.5 | 1.0 | 1.2 | 1.6 | 1.0 | 28.1±2 | 1097 |
| 14×2.5 | 1.0 | 1.2 | 1.7 | 1.0 | 29.3±2 | 1218 |
| 16×2.5 | 1.0 | 1.2 | 1.8 | 1.0 | 30.8±2 | 1328 |
| 19×2.5 | 1.0 | 1.2 | 1.8 | 1.0 | 31.6±2 | 1517 |
| 20×2.5 | 1.0 | 1.2 | 1.9 | 1.0 | 33.8±2 | 1622 |
| 23×2.5 | 1.0 | 1.4 | 2.0 | 1.0 | 36.7±2 | 1895 |
| 24×2.5 | 1.0 | 1.4 | 2.0 | 1.0 | 37.8±2 | 1943 |
| 27×2.5 | 1.0 | 1.4 | 2.0 | 1.0 | 37.4±2 | 2069 |
| 30×2.5 | 1.0 | 1.4 | 2.1 | 1.0 | 40.1±2 | 2347 |
| 33×2.5 | 1.0 | 1.4 | 2.2 | 1.0 | 41.6±2 | 2510 |
| 37×2.5 | 1.0 | 1.4 | 2.3 | 1.0 | 43.2±2 | 2741 |
| 44×2.5 | 1.0 | 1.4 | 2.4 | 1.0 | 48.2±2 | 3229 |

NEK 606:2004

N

Standard

Zero

Halogen Free IEC60754-1

IEC 60092-351

N

Standard

Low Corrosivity IEC60754-2

IEC 60092-353

N

Standard

Low Smoke Emission IEC 61034-1&2

IEC 60092-359

N

Standard

Flame Retardancy IEC60332-1

Water Tightness VG 95218-29

Reduced Fire Propagation IEC60332-3-22

W	E

Circuit Integrity IEC 60331-21