ADDISON

600/1000V Mica+XLPE Insulated, LSZH Sheathed Power Cables (2-4 cores)

FFX400 1mRZ1-R (CU/MGT+XLPE/LSZH 600/1000V Class 2)

FFX400 1mRMZ1-R (CU/MGT+XLPE/LSZH/SWA/LSZH 600/1000V Class 2)

APPLICATION

This cable is designed for areas where the integrity of the electrical properties circuit is critical in maintaining power supply. Applications can be found in emergency lightings, control and power circuits, power stations, fire alarm systems, underground tunnels, communications systems, sewage treatment plants, lifts, escalators, and high-rise buildings.

STANDARDS

Basic design to IEC 60502-1/BS 7846

FIRE PERFORMANCE

|  | IEC 60331-21; BS 6387 CWZ; DIN VDE 0472-814(FE180); |
| --- | --- |
| Circuit Integrity | CEI 20-36/2-1; SS229-1; NBN C 30-004 (cat. F3); |
|  | NF C32-070-2.3(CR1); BS 7846-(F2) |
| System circuit integrity | DIN 4102-12, E30 depending on lay system |

Flame Retardance (Single Vertical EN 60332-1-2; IEC 60332-1-2; BS EN 60332-1-2;

Wire Test) VDE 0482-332-1 ; NBN C 30-004 (cat. F1); NF C32-070-2.1(C2); CEI 20-35/1-2; EN 50265-2-1*; DIN VDE 0482-265-2-1*

| Reduced Fire Propagation | EN 60332-3-24 (cat. C); IEC 60332-3-24; BS EN 60332-3-24; |  |
| --- | --- | --- |
| (Vertically-mounted bundled wires VDE 0482-332-3; NBN C 30-004 (cat. F2); NF C32-070-2.2(C1); |  |  |
| & cable test) | CEI 20-22/3-4; EN 50266-2-4*; DIN VDE 0482-266-2-4 |  |
| Halogen Free | IEC 60754-1; EN 50267-2-1; DIN VDE 0482-267-2-1; |  |
|  | CEI 20-37/2-1 ; BS 6425-1* |  |
| No Corrosive Gas Emission | IEC 60754-2; EN 50267-2-2; DIN VDE 0482-267-2-2; |  |
|  | CEI 20-37/2-2 ; BS 6425-2* |  |
| Minimum Smoke Emission | IEC 61034-1&2; EN 61034 -1&2; DIN VDE 0482-1034-1&2; |  |
|  | CEI 20-37/3-1&2; EN 50268-1&2*; BS 7622-1&2* |  |
| No Toxic gases | NES 02-713; NF C 20-454 |  |

Note: Asterisk * denotes superseded standard.

44	Caledonian   sales@caledonian-cables.net   uk@caledonian-cables.net

Caledonian

Fire Resistant Power & Control Cables

www.caledonian-tech.net	www.caledonian-tech.com

VOLTAGE RATING

600/1000V

CABLE CONSTRUCTION

Conductor: Plain annealed copper wire, stranded according to IEC(EN) 60228 class 2.

Insulation: Mica glass tape covered by extruded cross-linked XLPE compound

Cabling: The cores are cabled together in concentric layers with suitable non-hygroscopic fillers.

Inner Sheath(optional): Thermoplastic LSZH compound type LTS3 as per BS 7655-6.1 Armouring(optional): Galvanized steel wire armour

Outer Sheath: Thermoplastic LSZH compound type LTS3 as per BS 7655-6.1 (Thermosetting LSZH compound type SW2-SW4 as per BS 7655-2.6 can be offered.)

COLOUR CODE

Insulation Colour

2 - Core: (Brown & Blue)

3 - Core: (Brown, Black & Grey)

4 - Core: (Brown, Black, Grey & Blue)

Sheath Colour

Orange (other colors upon request)

Physical AND THERMAL PROPERTIES

Temperature range during operation (fixed state):-30°C – +90°C

Temperature range during installation (mobile state): -20°C – +50°C

Minimum bending radius: 8 x Overall Diameter (unarmoured cable)

10 x Overall Diameter (armoured cable)

Electrical PROPERTIES

| Dielectric test: | 3500 | V r.m.s. x 5’ (core/core) |
| --- | --- | --- |
| Insulation resistance | 1000 | MΩ x km (at 20°C) |
| Short circuit temperature | 250°C |  |

CONSTRUCTION PARAMETERS

|  | Conductor |  |  | FFX400 1mRZ1-R |  | FFX400 1mRMZ1-R |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Unarmoured Cable |  | Armoured Cable |  |  |
|  | No./ |  | Nominal | Nominal |  | Nominal |  |  |
| Nominal | Nominal | Dia. of |  |  | Approx. |  | Approx. |  |
|  |  |  | Insulation | Overall |  | Overall |  |  |
| Area | Diameter of | Conductor |  |  | Weight |  | Weight |  |
|  |  |  | Thickness | Diameter |  | Diameter |  |  |
|  | Strands |  |  |  |  |  |  |  |
| mm2 | No./mm | mm | mm | mm | kg/km | mm | kg/km |  |
|  |  |  | 2-CORE |  |  |  |  |  |
| 1.5 | 7/0.53 | 1.59 | 0.7 | 12.2 | 150 | 15.3 | 390 |  |
| 2.5 | 7/0.67 | 2.01 | 0.7 | 12.6 | 180 | 16.5 | 450 |  |
| 4 | 7/0.85 | 2.55 | 0.7 | 14.7 | 250 | 17.6 | 525 |  |

ADDISON	45

ADDISON

| 6 | 7/1.04 | 3.12 | 0.7 | 16.2 | 290 | 18.8 |  | 620 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 10 | 7/1.35 | 4.05 | 0.7 | 17.1 | 450 | 21 |  | 800 |
| 16 | 7/1.70 | 5.1 | 0.7 | 19.2 | 550 | 23 |  | 1100 |
| 25 | 7/2.14 | 6.42 | 0.9 | 20 | 680 | 27 |  | 1480 |
| 35 | 19/1.53 | 7.65 | 0.9 | 22 | 940 | 30 |  | 2000 |
| 50 | 19/1.78 | 8.9 | 1 | 24 | 1250 | 33 |  | 2450 |
| 70 | 19/2.14 | 10.7 | 1.1 | 27 | 1700 | 37 |  | 3200 |
| 95 | 19/2.52 | 12.6 | 1.1 | 31 | 2300 | 42 |  | 4350 |
| 120 | 37/2.03 | 14.21 | 1.2 | 36 | 3150 | 48 |  | 6500 |
|  |  |  | 3-CORE |  |  |  |  |  |
| 1.5 | 7/0.53 | 1.59 | 0.7 | 12.3 | 170 |  | 16.5 | 420 |
| 2.5 | 7/0.67 | 2.01 | 0.7 | 13.8 | 200 |  | 17 | 500 |
| 4 | 7/0.85 | 2.55 | 0.7 | 15.2 | 300 |  | 18.5 | 600 |
| 6 | 7/1.04 | 3.12 | 0.7 | 16.8 | 380 |  | 19.8 | 785 |
| 10 | 7/1.35 | 4.05 | 0.7 | 18 | 550 |  | 22.6 | 1030 |
| 16 | 1/1.70 | 5.1 | 0.7 | 21 | 760 |  | 25 | 1370 |
| 25 | 7/2.14 | 6.42 | 0.9 | 22 | 960 |  | 29 | 1900 |
| 35 | 19/1.53 | 7.65 | 0.9 | 24 | 1300 |  | 32 | 2300 |
| 50 | 19/1.78 | 8.9 | 1 | 28 | 1700 |  | 35 | 2900 |
| 70 | 19/2.14 | 10.7 | 1.1 | 31 | 2400 |  | 40 | 4000 |
| 95 | 19/2.52 | 12.6 | 1.1 | 36 | 3250 |  | 45 | 5400 |
| 120 | 37/2.03 | 14.21 | 1.2 | 38 | 4000 |  | 49 | 6450 |
| 150 | 37/2.25 | 15.75 | 1.4 | 42 | 5000 |  | 55 | 8200 |
| 185 | 37/2.52 | 17.64 | 1.6 | 47 | 6100 |  | 60 | 9800 |
| 240 | 61/2.25 | 20.25 | 1.7 | 52 | 8000 |  | 68 | 12300 |
| 300 | 61/2.52 | 22.68 | 1.8 | 59 | 9850 |  | 74 | 14800 |
| 400 | 61/2.85 | 25.65 | 2 | 63 | 13000 |  | 83 | 17600 |
|  |  |  | 4-CORE |  |  |  |  |  |
| 1.5 | 7/0.53 | 1.59 | 0.7 | 14.3 | 210 |  | 16 | 475 |
| 2.5 | 7/0.67 | 2.01 | 0.7 | 15.2 | 270 |  | 17.8 | 570 |
| 4 | 7/0.85 | 2.55 | 0.7 | 17.2 | 380 |  | 19.8 | 690 |
| 6 | 7/1.04 | 3.12 | 0.7 | 19 | 440 |  | 21 | 940 |
| 10 | 7/1.35 | 4.05 | 0.7 | 20.6 | 670 |  | 23.3 | 1200 |
| 16 | 1/1.70 | 5.1 | 0.7 | 23.6 | 820 |  | 26.5 | 1400 |
| 25 | 7/2.14 | 6.42 | 0.9 | 26 | 1320 |  | 30.5 | 2400 |
| 35 | 19/1.53 | 7.65 | 0.9 | 29 | 1730 |  | 34 | 2800 |
| 50 | 19/1.78 | 8.9 | 1 | 32 | 2300 |  | 38 | 3500 |

46	Caledonian   sales@caledonian-cables.net   uk@caledonian-cables.net

Caledonian

ADDISON

ElectricAl PROPERTIES

Conductor Operating Temperature : 90°C Ambient Temperature : 30°C

FFX400 1mRZ1-R Current-Carrying Capacities (Amp)

Fire Resistant Power & Control Cables

www.caledonian-tech.net	www.caledonian-tech.com

| 70 | 19/2.14 | 10.7 | 1.1 | 38 | 3180 | 44 | 5300 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 95 | 19/2.52 | 12.6 | 1.1 | 41.9 | 4370 | 48.5 | 6700 |
| 120 | 37/2.03 | 14.21 | 1.2 | 44 | 5400 | 54 | 8500 |
| 150 | 37/2.25 | 15.75 | 1.4 | 50.8 | 6500 | 59 | 10000 |
| 185 | 37/2.52 | 17.64 | 1.6 | 55 | 8200 | 64.5 | 12200 |
| 240 | 61/2.25 | 20.25 | 1.7 | 60.5 | 10600 | 74 | 15400 |
| 300 | 61/2.52 | 22.68 | 1.8 | 68.5 | 13200 | 82 | 19500 |
| 400 | 61/2.85 | 25.65 | 2 | 76 | 17000 | 92 | 25500 |

|  | Reference |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Method 4 | Reference Method 3 |  |  |  | Reference Method 11 |  |  |
|  | (enclosed in |  |  | Reference Method 1 |  |  |  |  |
|  | an conduit |  |  | (clipped direct) |  |  |  |  |
|  | insulated |  |  |  |  |  |  |  |
|  |  | (enclosed in conduit on |  |  |  | (on a perforated cable |  |  |
| Nominal | wall etc) | a wall or ceiling, or in |  |  |  | tray), or Reference |  |  |
| Cross |  | trunking) |  |  |  | Method 13 (free air) |  |  |
| Section |  |  |  |  |  | one 2-core | one |  |
| Area |  |  |  |  | one 3-core |  | 3-core |  |
|  | one 3-core | one 2-core | one 3-core | one 2-core | cable or | cable | cable or |  |
|  | cable or one | cable single | cable or one | cable single | one 4-core | singlephase | one |  |
|  | 4-core cable | phase a.c. or | 4-core cable | phase a.c. or | cable |  |  |  |
|  |  |  |  |  |  | a.c. or | 4-core |  |
|  | 3-phase a.c. | d.c. | 3-phase a.c. | d.c. | 3-phase |  |  |  |
|  |  |  |  |  |  |  | cable |  |
|  |  |  |  |  | a.c. |  |  |  |
|  |  |  |  |  |  | d.c. | 3-phase |  |
|  |  |  |  |  |  |  | a.c. |  |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  |
| mm2 | A | A | A | A | A | A | A |  |
| 1.5 | 16.5 | 22 | 19.5 | 24 | 22 | 26 | 23 |  |
| 2.5 | 22 | 30 | 26 | 33 | 30 | 36 | 32 |  |
| 4 | 30 | 40 | 35 | 45 | 40 | 49 | 42 |  |
| 6 | 38 | 51 | 44 | 58 | 52 | 63 | 54 |  |
| 10 | 51 | 69 | 60 | 80 | 71 | 86 | 75 |  |
| 16 | 68 | 91 | 80 | 107 | 96 | 115 | 100 |  |
| 25 | 89 | 119 | 105 | 138 | 119 | 149 | 127 |  |
| 35 | 109 | 146 | 128 | 171 | 147 | 185 | 158 |  |
| 50 | 130 | 175 | 154 | 209 | 179 | 225 | 192 |  |

47

ADDISON

| 70 | 164 | 221 | 194 | 269 | 229 | 289 | 246 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 95 | 197 | 265 | 233 | 328 | 278 | 352 | 298 |
| 120 | 227 | 305 | 268 | 382 | 322 | 410 | 346 |
| 150 | 259 | 334 | 300 | 441 | 371 | 473 | 399 |
| 185 | 295 | 384 | 340 | 506 | 424 | 542 | 456 |
| 240 | 346 | 459 | 398 | 599 | 500 | 641 | 538 |
| 300 | 396 | 532 | 455 | 693 | 576 | 741 | 621 |
| 400 | - | 625 | 536 | 803 | 667 | 865 | 741 |

Voltage Drop (Per Amp Per Meter)

| Nominal Cross | 2-core | 2-core cable single-phase a.c |  |  | 3-core or 4-core cable 3-phase |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Section Area | cable d.c. |  |  |  |  | a.c. |  |  |
| 1 | 2 |  | 3 |  |  | 4 |  |  |
| mm2 | mV/A/m |  | mV/A/m |  |  | mV/A/m |  |  |
| 1.5 | 31 |  | 31 |  |  | 27 |  |  |
| 2.5 | 19 |  | 19 |  |  | 16 |  |  |
| 4 | 12 |  | 12 |  |  | 10 |  |  |
| 6 | 7.9 |  | 7.9 |  |  | 6.8 |  |  |
| 10 | 4.7 |  | 4.7 |  |  | 4 |  |  |
| 16 | 2.9 |  | 2.9 |  |  | 2.5 |  |  |
|  |  | r | x | z | r | x | z |  |
| 25 | 1.85 | 1.85 | 0.16 | 1.9 | 1.6 | 0.14 | 1.65 |  |
| 35 | 1.35 | 1.35 | 0.155 | 1.35 | 1.15 | 0.135 | 1.15 |  |
| 50 | 0.98 | 0.99 | 0.155 | 1 | 0.86 | 0.135 | 0.87 |  |
| 70 | 0.67 | 0.67 | 0.15 | 0.69 | 0.59 | 0.13 | 0.6 |  |
| 95 | 0.49 | 0.5 | 0.15 | 0.52 | 0.43 | 0.13 | 0.45 |  |
| 120 | 0.39 | 0.4 | 0.145 | 0.42 | 0.34 | 0.13 | 0.37 |  |
| 150 | 0.31 | 0.32 | 0.145 | 0.35 | 0.28 | 0.125 | 0.3 |  |
| 185 | 0.25 | 0.26 | 0.145 | 0.29 | 0.22 | 0.125 | 0.26 |  |
| 240 | 0.195 | 0.2 | 0.14 | 0.24 | 0.175 | 0.125 | 0.21 |  |
| 300 | 0.155 | 0.16 | 0.14 | 0.21 | 0.14 | 0.12 | 0.185 |  |
| 400 | 0.12 | 0.13 | 0.14 | 0.19 | 0.115 | 0.12 | 0.165 |  |

FFX400 1mRMZ1-R

Current-Carrying Capacities (Amp)

48	Caledonian  sales@caledonian-cables.net   uk@caledonian-cables.net

Caledonian

Fire Resistant Power & Control Cables

www.caledonian-tech.net	www.caledonian-tech.com

|  |  |  |  |  |  |  | Reference Method |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Reference Method |  |  |  | 11 (on a perforated |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Nominal Cross |  |  |  |  |  |  | horizontal cable |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Section Area |  |  |  |  | 1 (clipped |  | tray or Reference |  |  |  | In single-way ducts |  |  | Laid direct in ground |  |  |  |  |  |  |
|  |  |  |  |  | direct) |  | Method 13 [free |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | air] ) |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | one |  |  | one |  |  |  | one |  |  |  | one |  |  |  |  |  |
|  |  |  |  | 2-core |  | one 3-core | 2-core |  | one 3-core |  | 2-core | one 3-core |  | 2-core |  |  | one 3-core |  |  |  |
|  |  |  |  | cable |  | or 4-core | cable |  | or 4-core |  | cable | or 4-core |  | cable |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | or 4-core |  |  |
|  |  |  |  | single |  | cable | single |  | cable |  | single | cable |  | single |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | cable |  |
|  |  |  |  | phase |  | 3-phase | phase |  | 3-phase |  | phase | 3-phase |  | phase |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 3-phase a.c. |  |  |  |  |
|  |  |  |  | a.c. or |  | a.c. | a.c. or |  | a.c. |  | a.c. or | a.c. |  | a.c. or |  |  |  |  |  |  |
|  |  |  |  | d.c. |  |  | d.c. |  |  |  | d.c. |  |  |  | d.c. |  |  |  |  |  |
| 1 |  |  |  |  | 2 | 3 | 4 |  | 5 |  | 6 | 7 |  | 8 |  |  |  |  | 9 |  |
| mm2 |  |  |  |  | A | A | A |  | A |  | A | A |  |  | A |  |  |  | A |  |
| 1.5 |  |  |  |  | 27 | 23 | 29 |  | 25 |  | - | 23 |  | - |  |  |  |  | 28 |  |
| 2.5 |  |  |  |  | 36 | 31 | 39 |  | 33 |  | - | 30 |  | - |  |  |  |  | 36 |  |
| 4 |  |  |  |  | 49 | 42 | 52 |  | 44 |  | - | 40 |  | - |  |  |  |  | 48 |  |
| 6 |  |  |  |  | 62 | 53 | 66 |  | 56 |  | - | 50 |  | - |  |  |  |  | 60 |  |
| 10 |  |  |  |  | 85 | 73 | 90 |  | 78 |  | - | 65 |  | - |  |  |  |  | 80 |  |
| 16 |  |  |  | 110 |  | 94 | 115 |  | 99 |  | 115 | 94 |  | 140 |  |  |  |  | 115 |  |
| 25 |  |  |  | 146 |  | 124 | 152 |  | 131 |  | 145 | 125 |  | 180 |  |  |  |  | 150 |  |
| 35 |  |  |  | 180 |  | 154 | 188 |  | 162 |  | 175 | 150 |  | 215 |  |  |  |  | 180 |  |
| 50 |  |  |  | 219 |  | 187 | 228 |  | 197 |  | 210 | 175 |  | 255 |  |  |  |  | 215 |  |
| 70 |  |  |  | 279 |  | 238 | 291 |  | 251 |  | 260 | 215 |  | 315 |  |  |  |  | 265 |  |
| 95 |  |  |  | 338 |  | 289 | 354 |  | 304 |  | 310 | 260 |  | 380 |  |  |  |  | 315 |  |
| 120 |  |  |  | 392 |  | 335 | 410 |  | 353 |  | 355 | 300 |  | 430 |  |  |  |  | 360 |  |
| 150 |  |  |  | 451 |  | 386 | 472 |  | 406 |  | 400 | 335 |  | 480 |  |  |  |  | 405 |  |
| 185 |  |  |  | 515 |  | 441 | 539 |  | 463 |  | 455 | 380 |  | 540 |  |  |  |  | 460 |  |
| 240 |  |  |  | 607 |  | 520 | 636 |  | 546 |  | 520 | 440 |  | 630 |  |  |  |  | 530 |  |
| 300 |  |  |  | 698 |  | 599 | 732 |  | 628 |  | 590 | 495 |  | 700 |  |  |  |  | 590 |  |
| 400 |  |  |  | 787 |  | 673 | 847 |  | 728 |  | 660 | 560 |  | 790 |  |  |  |  | 670 |  |
| Voltage Drop (Per Amp Per Meter) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 2 cables, |  |  |  | 3 or 4 |  |
| Nominal |  |  |  |  |  |  |  |  |  |  |  |  |  |  | single- |  |  |  | cables, |  |
|  |  | 2-core |  |  |  |  |  |  |  |  |  |  |  |  | phase |  |  |  | 3-phase |  |
| Cross |  |  |  |  | 2 cables, single-phase a.c. |  |  |  |  | 3 or 4 cables, 3-phase a.c. |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | a.c. |  |  |  | a.c. |  |
| Section | cable d.c. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | In ducts |  |  |  | In ducts |  |
| Area |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | or |  |  |  | or |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | in ground |  |  |  | in ground |  |
| 1 |  | 2 |  |  |  | 3 |  |  |  |  | 4 |  |  |  | 5 |  |  |  | 6 |  |
| mm2 |  | mV/A/m |  |  |  | mV/A/m |  |  |  |  | mV/A/m |  |  |  | mV/A/m |  |  |  | mV/A/m |  |
| 1.5 |  | 31 |  |  |  | 31 |  |  |  |  | 27 |  |  |  | 31 |  |  |  | 25 |  |
| 2.5 |  | 19 |  |  |  | 19 |  |  |  |  | 16 |  |  |  | 19 |  |  |  | 15 |  |
| 4 |  | 12 |  |  |  | 12 |  |  |  |  | 10 |  |  |  | 12 |  |  |  | 9.7 |  |

ADDISON	49

ADDISON

| 6 | 7.9 |  | 7.9 |  |  | 6.8 |  | 7.9 | 6.5 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 10 | 4.7 |  | 4.7 |  |  | 4 |  | 4.7 | 3.9 |
| 16 | 2.9 |  | 2.9 |  |  | 2.5 |  | 2.9 | 2.6 |
|  |  | r | x | z | r | x | z |  |  |
| 25 | 1.85 | 1.35 | 0.16 | 1.9 | 1.6 | 0.14 | 1.65 | 1.9 | 1.6 |
| 35 | 1.35 | 1.35 | 0.155 | 1.35 | 1.15 | 0.135 | 1.15 | 1.35 | 1.2 |
| 50 | 0.98 | 0.99 | 0.155 | 1 | 0.86 | 0.135 | 0.87 | 1 | 0.87 |
| 70 | 0.67 | 0.67 | 0.15 | 0.69 | 0.59 | 0.13 | 0.6 | 0.69 | 0.61 |
| 95 | 0.49 | 0.5 | 0.15 | 0.52 | 0.43 | 0.13 | 0.45 | 0.52 | 0.45 |
| 120 | 0.39 | 0.4 | 0.145 | 0.42 | 0.34 | 0.13 | 0.37 | 0.42 | 0.36 |
| 150 | 0.31 | 0.32 | 0.145 | 0.35 | 0.28 | 0.125 | 0.3 | 0.35 | 0.3 |
| 185 | 0.25 | 0.26 | 0.145 | 0.29 | 0.22 | 0.125 | 0.26 | 0.29 | 0.25 |
| 240 | 0.195 | 0.2 | 0.14 | 0.24 | 0.175 | 0.125 | 0.21 | 0.24 | 0.21 |
| 300 | 0.155 | 0.16 | 0.14 | 0.21 | 0.14 | 0.12 | 0.185 | 0.21 | 0.19 |
| 400 | 0.12 | 0.13 | 0.14 | 0.19 | 0.115 | 0.12 | 0.165 | 0.19 | 0.18 |

Note : r = conductor resistance at operating temperature x = reactance

z = impedance

|  | BS 7846 |
| --- | --- |
| 600/1000V | IECN60502-1 |

W

E

|  |  |  |  |  | Circuit Integrity | Reduced Fire Propagation | Flame Retardancy |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | NF C32-070-2.2(C1) | NF C32-070-2.1(C2) |  |
| Rated Voltage |  |  |  | Standard | IEC 60331/BS 6387 |  |  |  |
|  |  |  |  |  | NF C32-070-2.3(CR1) | IEC60332-3-24/EN50266-2-4 IEC60332-1-2/EN50265-2-1 |  |  |

Zero

W

E

|  |  |  | Low Corrosivity | Low Smoke Emission |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | Halogen Free |  |  |
|  | Low Toxicity |  | IEC60754-2 | IEC 61034-1&2 | IEC60754-1 | Functional Integrity |  |
|  |  |  | EN50267-2-2/3 |  |  |  |  |
| NES 02-713/NF C 20-454 |  |  |  | EN 50268-1&2/NF C32-073 |  |  |  |
|  |  |  | NF C 32-074 |  | EN50267-2-1 | DIN 4102-12 |  |

50	Caledonian   sales@caledonian-cables.net   uk@caledonian-cables.net