Caledonian

Fire Resistant Coaxial Cables

www.caledonian-tech.net	www.caledonian-tech.com

Fire Resistant RG11 A/U Coaxial Cables

RG11 A/U FR

Plain Copper Wire Braid Screen

(PE+Silicone Rubber)/FEP Insulation

Tinned Copper

LSZH Outer Sheath

APPLICATION

The cables are designed for CCTV, security, smoke detection and evacuation monitoring applications, where continued functionality is required during a fire situationDue. to the zero halogen low smoke construction, this cable is ideal for use in public, commercial and industrial environments.

Standards

Basic design to MIL-C-17

FIRE PERFORMANCE

|  | IEC 60331-23; BS 6387 CWZ; DIN VDE 0472-814(FE180); |  |
| --- | --- | --- |
| Circuit Integrity | CEI 20-36/2-1; SS229-1; NBN C 30-004 (cat. F3); |  |
|  | NF C32-070-2.3(CR1) |  |
| System circuit integrity | DIN 4102-12, E30 depending on lay system |  |
| Flame Retardance (Single Vertical | EN 60332-1-2; IEC 60332-1-2; BS EN 60332-1-2; VDE |  |
| Wire Test) | 0482-332-1 ; NBN C 30-004 (cat. F1); NF C32-070-2.1(C2); |  |
|  | CEI 20-35/1-2; EN 50265-2-1*; DIN VDE 0482-265-2-1* |  |
| Reduced Fire Propagation | EN 60332-3-24 (cat. C); IEC 60332-3-24; BS EN 60332-3-24; |  |
| (Vertically-mounted bundled wires | VDE 0482-332-3; NBN C 30-004 (cat. F2); NF C32-070-2.2(C1); |  |
| & cable test) | CEI 20-22/3-4; EN 50266-2-4*; DIN VDE 0482-266-2-4 |  |
| Halogen Free | IEC 60754-1; EN 50267-2-1; DIN VDE 0482-267-2-1; |  |
|  | CEI 20-37/2-1 ; BS 6425-1* |  |
| No Corrosive Gas Emission | IEC 60754-2; EN 50267-2-2; DIN VDE 0482-267-2-2; |  |
|  | CEI 20-37/2-2 ; BS 6425-2* |  |
| Minimum Smoke Emission | IEC 61034-1&2; EN 61034 -1&2; DIN VDE 0482-1034-1&2; |  |
|  | CEI 20-37/3-1&2; EN 50268-1&2*; BS 7622-1&2* |  |
| No Toxic gases | NES 02-713; NF C 20-454 |  |

Note: Asterisk * denotes superseded standard.

ADDISON   129

ADDISON

CABLE CONSTRUCTION

Conductors: Tinned copper copper wire, stranded according to IEC(EN) 60228 class 2.

Insulation: Low density PE wrapped with fire resistant silicone rubber compound type EI2 as per BS 7655-1.1 or fluoropolymer(FEP) compound.

Binder: Glass tape

Overall Screen: Plain copper wire braid

Outer Sheath: Thermoplastic LSZH compound type LTS3 as per BS 7655-6.1 (Thermosetting LSZH compound type SW2-SW4 as per BS 7655:section 2.6 can be offered.)

Physical AND THERMAL PROPERTIES

Temperature range during operation (fixed state):-30°C - +70°C

Temperature range during installation (mobile state): -5ºC - +60ºC

Minimum bending radius: 8 x Overall Diameter

Electrical Properties

| Impedance | 75±5Ω |
| --- | --- |
| Capacitance | 67 nF/km |
| Velocity ratio(%) | 66 |
| Insulation resistance | >2000 Mohm.Km |
| Shield coverage | 97% |
| DC resistance |  |
| Inner conductor | 20.5 Ω/km |
| Outer conductor | 4.5 Ω/km |

Attenuation

| Frequency(MHz) | Attenuation (dB/100 m) | Attenuation (dB/100ft) |
| --- | --- | --- |
| 50 | 4.2 | 1.28 |
| 100 | 6.2 | 1.89 |
| 200 | 9.3 | 2.84 |
| 400 | 13.8 | 4.21 |
| 500 | 15.5 | 4.73 |
| 600 | 17.1 | 5.21 |
| 860 | 20.1 | 6.13 |
| 1000 | 23.4 | 7.13 |

130	Caledonian   sales@caledonian-cables.net   uk@caledonian-cables.net

Caledonian

Fire Resistant Coaxial Cables

www.caledonian-tech.net	www.caledonian-tech.com

Return Loss

| Frequency(MHz) |  |  | Return Loss (dB) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 30-300 MHz |  |  | >30dB |  |  |  |  |  |
| 300-600 MHz |  |  | >27dB |  |  |  |  |  |
| 600-900 MHz |  |  | >25dB |  |  |  |  |  |
| CONSTRUCTION PARAMETERS |  |  |  |  |  |  |  |  |
| Cable | Conductor |  | Nominal | Nominal |  | Nominal | Approx. |  |
|  |  |  | Insulation | Screen |  | Overall |  |  |
| Code | Diameter |  |  |  |  |  | Weight |  |
|  |  |  | Diameter | No.x Diameter |  | Diameter |  |  |
|  | mm |  | mm | No. x mm |  | mm | kg/km |  |
| RG11 A/U FR | 7 x 0.40 |  | 7.25 ± 0.18 | 192 x 0.18 |  | 10.3 ± 0.18 | 150 |  |

300/500V	NMIL-C-17

W

E

|  |  | Circuit Integrity | Reduced Fire Propagation | Flame Retardancy |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | NF C32-070-2.2(C1) | NF C32-070-2.1(C2) |  |  |
| Rated Voltage |  | IEC 60331/BS 6387 |  |  |  |  |
|  |  |  | IEC60332-3-24/EN50266-2-4 IEC60332-1-2/EN50265-2-1 |  |  |  |
|  | Standard | NF C32-070-2.3(CR1) |  |  |  |  |
|  |  |  | Zero | W | E |  |
|  | Low Corrosivity | Low Smoke Emission | Halogen Free |  |  |  |
| Low Toxicity | IEC60754-2 |  |  |  |  |  |
|  |  | IEC 61034-1&2 | IEC60754-1 | Functional Integrity |  |  |
|  | EN50267-2-2/3 |  |  |  |  |  |
| NES 02-713/NF C 20-454 | NF C 32-074 | EN 50268-1&2/NF C32-073 | EN50267-2-1 |  | DIN 4102-12 |  |

ADDISON   131