Caledonian

Fire Resistant Signal & Data Cables

www.caledonian-tech.net	www.caledonian-tech.com

Fire Resistant RS485 Databus Cables

APPLICATION

The cables are designed for RS485 data connections where continued functionality is required during a fire situation. This cable combines low capacitance insulation with one of the highest levels of screening to provide high speed, interference free, data transmission where continued functionality is required during a fire situation.

STANDARDS

Basic design to EIA/TIA 485

FIRE PERFORMANCE

|  | IEC 60331-23; BS 6387 CWZ; DIN VDE 0472-814(FE180); |  |
| --- | --- | --- |
| Circuit Integrity | CEI 20-36/2-1; SS229-1; NBN C 30-004 (cat. F3); |  |
|  | NF C32-070-2.3(CR1) |  |
| System circuit integrity | DIN 4102-12, E30 depending on lay system |  |
| Flame Retardance (Single Vertical | EN 60332-1-2; IEC 60332-1-2; BS EN 60332-1-2; VDE |  |
| Wire Test) | 0482-332-1 ; NBN C 30-004 (cat. F1); NF C32-070-2.1(C2); |  |
|  | CEI 20-35/1-2; EN 50265-2-1*; DIN VDE 0482-265-2-1* |  |
| Reduced Fire Propagation | EN 60332-3-24 (cat. C); IEC 60332-3-24; BS EN 60332-3-24; |  |
| (Vertically-mounted bundled wires | VDE 0482-332-3; NBN C 30-004 (cat. F2); NF C32-070-2.2(C1); |  |
| & cable test) | CEI 20-22/3-4; EN 50266-2-4*; DIN VDE 0482-266-2-4 |  |
| Halogen Free | IEC 60754-1; EN 50267-2-1; DIN VDE 0482-267-2-1; |  |
|  | CEI 20-37/2-1 ; BS 6425-1* |  |
| No Corrosive Gas Emission | IEC 60754-2; EN 50267-2-2; DIN VDE 0482-267-2-2; |  |
|  | CEI 20-37/2-2 ; BS 6425-2* |  |
| Minimum Smoke Emission | IEC 61034-1&2; EN 61034 -1&2; DIN VDE 0482-1034-1&2; |  |
|  | CEI 20-37/3-1&2; EN 50268-1&2*; BS 7622-1&2* |  |
| No Toxic gases | NES 02-713; NF C 20-454 |  |

Note: Asterisk * denotes superseded standard..

CABLE CONSTRUCTION

Multipair RS 485 Overall Screened Databus Cable

Conductors: tinned copper wire, stranded according to IEC(EN) 60228 class 2.

ADDISON   115

ADDISON

Insulation: mica glass tape wrapped with PE or PE wrapped with silicone rubber insulation. Cabling Elements: Insulated cores are twisted to form pairs with varying lay length to minimize crosstalk. Two pair cable had four cores laid in quad formation.

Cabling: Pairs are cabled together in concentric layers.

Overall screen: Aluminum/polyester tape with tinned copper drain wire.

Outer Sheath: Thermoplastic LSZH compound type LTS3 as per BS 7655-6.1 (Thermosetting LSZH compound type SW2-SW4 as per BS 7655-2.6 can be offered.)

Multipair RS 485 Overall Double Screened Databus Cable

Conductors: tinned copper wire, stranded according to IEC(EN) 60228 class 2. Insulation: mica glass tape wrapped with PE or PE wrapped with silicone rubber insulation.

Cabling Elements: Insulated cores are twisted to form pairs with varying lay length to minimize crosstalk. Two pair cable had four cores laid in quad formation.

Cabling: Pairs are cabled together in concentric layers. Overall screen: Aluminium/polyester tape+copper wire braid.

Outer Sheath: Thermoplastic LSZH compound type LTS3 as per BS 7655-6.1 (Thermosetting LSZH compound type SW2-SW4 as per BS 7655-2.6 can be offered.)

Multipair RS 485 Individual & Overall screened Databus Cable Conductors: tinned copper wire, stranded according to IEC(EN) 60228 class 2.

Insulation: mica glass tape wrapped with PE or PE wrapped with silicone rubber insulation. Cabling Elements: Insulated cores are twisted to form pairs with varying lay length to minimize crosstalk. Two pair cable had four cores laid in quad formation.

Cabling: Pairs are cabled together in concentric layers. Individual Screen: Individual aluminium/polyester tape. Overall Screen: Copper wire braid.

outer Sheath: Thermoplastic LSZH compound type LTS3 as per BS 7655-6.1 (Thermosetting LSZH compound type SW2-SW4 as per BS 7655-2.6 can be offered.)

Multipair RS 485 Overall Screened Databus Cable

Conductors: tinned copper wire, stranded according to IEC(EN) 60228 class 2. Insulation: mica glass tape wrapped with PE or PE wrapped with silicone rubber insulation.

Cabling Elements: Insulated cores are twisted to form pairs with varying lay length to minimize crosstalk. Two pair cable had four cores laid in quad formation.

Cabling: Pairs are cabled together in concentric layers. Overall Screen: Copper wire braid.

Outer Sheath: Thermoplastic LSZH compound type LTS3 as per BS 7655-6.1 (Thermosetting LSZH compound type SW2-SW4 as per BS 7655-2.6 can be offered.)

Physical AND THERMAL PROPERTIES

Temperature range during operation (fixed state):-20°C - +90°C

Temperature range during installation (mobile state): -5°C - +60°C

Minimum bending radius: 8 x Overall Diameter

116	Caledonian   sales@caledonian-cables.net   uk@caledonian-cables.net

Caledonian

Fire Resistant Signal & Data Cables

www.caledonian-tech.net	www.caledonian-tech.com

Electrical Properties

| Dielectric test | 1000 | V r.m.s. for 5’ (core-core) |
| --- | --- | --- |
|  | 1000 | V r.m.s. for 5’ (core-screen) |
| Impedance | 120Ω |  |
| Capacitance | 45 nF/km conductor to conductor |  |
|  | 90 nF/km conductor to shield |  |

CONSTRUCTION PARAMETERS

Multipair RS 485 Overall Screened Databus Cable

RE-m02Y(ST)H-FR / RE-m02YS(ST)H-FR

RE-S02Y(ST)H-FR / RE-S02YS(ST)H-FR

|  | Nominal |  |  | No./Nominal |  |  | Nominal |  |  | Nominal |  |  | Nominal |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| No.of | Cross |  |  |  |  |  |  |  |  |  |  |  |  | Approx. |  |  |
|  |  |  |  | Diameter of |  |  | Insulation |  |  | Sheath |  |  | Overall |  |  |  |
| pair x | Sectional |  |  |  |  |  |  |  |  |  |  |  |  | Weight |  |  |
|  |  |  |  | Strands |  |  | Thickness |  |  | Thickness |  |  | Diameter |  |  |  |
|  | Area |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | mm2 |  |  | No/mm |  |  | mm |  |  | mm |  |  | mm | kg/km |  |  |
| 1 | 0.22 |  |  | 7/0.2 |  |  | 0.55 |  |  | 0.40 |  |  | 4.6 | 29 |  |  |
| 2 | 0.22 |  |  | 7/0.2 |  |  | 0.55 |  |  | 0.40 |  |  | 8.1 | 60 |  |  |
| 4 | 0.22 |  |  | 7/0.2 |  |  | 0.55 |  |  | 0.40 |  |  | 9.6 | 100 |  |  |
| 1 | 0.50 |  |  | 16/0.2 |  |  | 0.55 |  |  | 0.40 |  |  | 5.2 | 44 |  |  |
| 2 | 0.50 |  |  | 16/0.2 |  |  | 0.55 |  |  | 0.40 |  |  | 9.3 | 91 |  |  |
| 4 | 0.50 |  |  | 16/0.2 |  |  | 0.55 |  |  | 0.40 |  |  | 11.1 | 158 |  |  |
| 1 | 0.75 |  |  | 24/0.2 |  |  | 0.55 |  |  | 0.40 |  |  | 5.6 | 56 |  |  |
| 2 | 0.75 |  |  | 24/0.2 |  |  | 0.55 |  |  | 0.40 |  |  | 10.3 | 117 |  |  |
| 4 | 0.75 |  |  | 24/0.2 |  |  | 0.55 |  |  | 0.40 |  |  | 12.2 | 207 |  |  |
| 1 | 1.00 |  |  | 30/0.2 |  |  | 0.55 |  |  | 0.40 |  |  | 5.8 | 61.4 |  |  |
| 2 | 1.00 |  |  | 30/0.2 |  |  | 0.55 |  |  | 0.40 |  |  | 10.6 | 128 |  |  |
| 4 | 1.00 |  |  | 30/0.2 |  |  | 0.55 |  |  | 0.40 |  |  | 12.5 | 228 |  |  |
| Multipair RS 485 Overall Double Screened Databus Cable |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| RE-m02Y(ST)CH-FR / RE-m02YS(ST)CH-FR |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| RE-S02Y(ST)CH-FR / RE-S02YS(ST)CH-FR |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Nominal |  |  | No./Nominal |  |  | Nominal |  |  | Nominal |  | Nominal |  |  |  |
| No.of |  | Cross |  |  |  |  |  |  |  |  |  |  |  |  | Approx. |  |
|  |  |  |  |  | Diameter of |  |  | Insulation |  |  | Sheath |  | Overall |  |  |  |
| pair x |  | Sectional |  |  |  |  |  |  |  |  |  |  |  |  | Weight |  |
|  |  |  |  |  | Strands |  |  | Thickness |  |  | Thickness |  | Diameter |  |  |  |
|  |  | Area |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | mm2 |  |  | No/mm |  |  | mm |  |  | mm |  | mm |  | kg/km |  |
| 1 |  | 0.22 |  |  | 7/0.2 |  |  | 0.55 |  |  | 0.40 |  | 5.0 |  | 45 |  |
| 2 |  | 0.22 |  |  | 7/0.2 |  |  | 0.55 |  |  | 0.40 |  | 8.6 |  | 88 |  |

ADDISON   117

ADDISON

|  | 4 |  | 0.22 |  | 7/0.2 |  |  |  | 0.55 |  |  | 0.40 | 10.1 |  | 134 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 1 |  | 0.50 |  | 16/0.2 |  |  |  | 0.55 |  |  | 0.40 | 5.6 |  | 61 |  |  |
|  | 2 |  | 0.50 |  | 16/0.2 |  |  |  | 0.55 |  |  | 0.40 | 9.8 |  | 124 |  |  |
|  | 4 |  | 0.50 |  | 16/0.2 |  |  |  | 0.55 |  |  | 0.40 | 11.5 |  | 197 |  |  |
|  | 1 |  | 0.75 |  | 24/0.2 |  |  |  | 0.55 |  |  | 0.40 | 6.1 |  | 75 |  |  |
|  | 2 |  | 0.75 |  | 24/0.2 |  |  |  | 0.55 |  |  | 0.40 | 10.7 |  | 154 |  |  |
|  | 4 |  | 0.75 |  | 24/0.2 |  |  |  | 0.55 |  |  | 0.40 | 12.7 |  | 250 |  |  |
|  | 1 |  | 1.00 |  | 30/0.2 |  |  |  | 0.55 |  |  | 0.40 | 6.3 |  | 81 |  |  |
|  | 2 |  | 1.00 |  | 30/0.2 |  |  |  | 0.55 |  |  | 0.40 | 11.0 |  | 166 |  |  |
|  | 4 |  | 1.00 |  | 30/0.2 |  |  |  | 0.55 |  |  | 0.40 | 13.0 |  | 273 |  |  |
| Multipair RS 485 Individual & Overall screened Databus Cable |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| RE-m02Y(ST)H pimf-FR / RE-m02YS(ST)H pimf-FR |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| RE-S02Y(ST)H pimf-FR / RE-S02YS(ST)H pimf-FR |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Nominal |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | No./Nominal |  |  | Nominal |  |  |  | Nominal | Nominal |  |  |  |  |
|  | No.of pair |  | Cross |  |  |  |  |  |  |  |  |  |  |  |  | Approx. |  |
|  |  |  |  |  | Diameter of |  |  | Insulation |  |  |  | Sheath | Overall |  |  |  |  |
|  | x |  | Sectional |  |  |  |  |  |  |  |  |  |  |  |  | Weight |  |
|  |  |  |  |  | Strands |  |  | Thickness |  |  |  | Thickness | Diameter |  |  |  |  |
|  |  |  | Area |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | mm2 |  | No/mm |  |  | mm |  |  |  | mm | mm |  |  | kg/km |  |
|  | 1 |  | 0.22 |  | 7/0.2 |  |  | 0.55 |  |  |  | 0.40 | 4.9 |  |  | 46 |  |
|  | 2 |  | 0.22 |  | 7/0.2 |  |  | 0.55 |  |  |  | 0.40 | 8.6 |  |  | 91 |  |
|  | 4 |  | 0.22 |  | 7/0.2 |  |  | 0.55 |  |  |  | 0.40 | 10.1 |  |  | 144 |  |
|  | 1 |  | 0.50 |  | 16/0.2 |  |  | 0.55 |  |  |  | 0.40 | 5.5 |  |  | 62 |  |
|  | 2 |  | 0.50 |  | 16/0.2 |  |  | 0.55 |  |  |  | 0.40 | 9.8 |  |  | 127 |  |
|  | 4 |  | 0.50 |  | 16/0.2 |  |  | 0.55 |  |  |  | 0.40 | 11.6 |  |  | 209 |  |
|  | 1 |  | 0.75 |  | 24/0.2 |  |  | 0.55 |  |  |  | 0.40 | 6.0 |  |  | 76 |  |
|  | 2 |  | 0.75 |  | 24/0.2 |  |  | 0.55 |  |  |  | 0.40 | 10.7 |  |  | 157 |  |
|  | 4 |  | 0.75 |  | 24/0.2 |  |  | 0.55 |  |  |  | 0.40 | 12.7 |  |  | 263 |  |
|  | 1 |  | 1.00 |  | 30/0.2 |  |  | 0.55 |  |  |  | 0.40 | 6.2 |  |  | 83 |  |
|  | 2 |  | 1.00 |  | 30/0.2 |  |  | 0.55 |  |  |  | 0.40 | 11.0 |  |  | 170 |  |
|  | 4 |  | 1.00 |  | 30/0.2 |  |  | 0.55 |  |  |  | 0.40 | 13.0 |  |  | 286 |  |
| Multipair RS 485 Overall Screened Databus Cable |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| RE-m02YCH-FR / RE-m02YSCH-FR |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| RE-S02YCH-FR / RE-S02YSCH-FR |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Nominal |  |  | No./Nominal |  | Nominal |  |  |  | Nominal |  | Nominal |  |  |  |
|  | No.of pair |  | Cross |  |  |  |  |  |  |  |  |  |  |  |  | Approx. |  |
|  |  |  |  |  |  | Diameter of |  | Insulation |  |  |  | Sheath |  | Overall |  |  |  |
|  | x |  | Sectional |  |  |  |  |  |  |  |  |  |  |  |  | Weight |  |
|  |  |  |  |  |  | Strands |  | Thickness |  |  |  | Thickness |  | Diameter |  |  |  |
|  |  |  | Area |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | mm2 |  |  | No/mm |  | mm |  |  |  | mm |  | mm |  | kg/km |  |
|  | 1 |  | 0.22 |  |  | 7/0.2 |  | 0.55 |  |  |  | 0.40 |  | 4.8 |  | 41 |  |
| 118 | Caledonian |  |  | sales@caledonian-cables.net |  |  |  | uk@caledonian-cables.net |  |  |  |  |  |  |  |  |  |

Caledonian

Fire Resistant Signal & Data Cables

www.caledonian-tech.net	www.caledonian-tech.com

| 2 | 0.22 | 7/0.2 | 0.55 | 0.40 | 8.4 | 82 |
| --- | --- | --- | --- | --- | --- | --- |
| 4 | 0.22 | 7/0.2 | 0.55 | 0.40 | 9.9 | 127 |
| 1 | 0.50 | 16/0.2 | 0.55 | 0.40 | 5.4 | 57 |
| 2 | 0.50 | 16/0.2 | 0.55 | 0.40 | 9.6 | 117 |
| 4 | 0.50 | 16/0.2 | 0.55 | 0.40 | 11.4 | 189 |
| 1 | 0.75 | 24/0.2 | 0.55 | 0.40 | 5.9 | 71 |
| 2 | 0.75 | 24/0.2 | 0.55 | 0.40 | 10.5 | 146 |
| 4 | 0.75 | 24/0.2 | 0.55 | 0.40 | 12.4 | 241 |
| 1 | 1.00 | 30/0.2 | 0.55 | 0.40 | 6.0 | 77 |
| 2 | 1.00 | 30/0.2 | 0.55 | 0.40 | 10.8 | 158 |
| 4 | 1.00 | 30/0.2 | 0.55 | 0.40 | 12.8 | 264 |

TYPE CODES

RE-A-B-D-FR

FR: Fire Resisting

Outer Sheath

H: LSZH

Screen

St: Aluminum tape C: Copper braid

Insulation

m02Y: Mica Tape+Foam PE S2Y: Silicone Rubber+Foam PE m02YS: Mica Tape+Foam Skin PE

S2YS: Silicone Rubber+Foam Skin PE

300/500V	NEIA/TIA485

W

E

|  |  | Circuit Integrity | Reduced Fire Propagation | Flame Retardancy |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | NF C32-070-2.2(C1) | NF C32-070-2.1(C2) |  |
| Rated Voltage | Standard | IEC 60331/BS 6387 |  |  |  |
|  |  | NF C32-070-2.3(CR1) | IEC60332-3-24/EN50266-2-4 | IEC60332-1-2/EN50265-2-1 |  |

Zero

W

E

|  | Low Corrosivity | Low Smoke Emission | Halogen Free |  |  |
| --- | --- | --- | --- | --- | --- |
| Low Toxicity | IEC60754-2 | IEC 61034-1&2 | IEC60754-1 | Functional Integrity |  |
|  | EN50267-2-2/3 |  |  |  |  |
| NES 02-713/NF C 20-454 | NF C 32-074 | EN 50268-1&2/NF C32-073 | EN50267-2-1 | DIN 4102-12 |  |

ADDISON   119