ADDISON

Fire Resistant UTP CAT5 Data Cables

FFX-CAT5UTP4P24FR

APPlICATION

The cables are desgined for structure wiring, compatible with all known connection systems according to EN 50173.

Based on the design for structured wiring (found in IEC 61156 and BS EN 50288), this cable brings together high frequency data transmission and circuit integrity in four pair cable that will continue to transmit data even when being directly attacked by fire.

STANDARDS

Basic design to EN50173

Fire Performance

|  |  |  | IEC 60331-23; BS 6387 CWZ; DIN VDE 0472-814(FE180); |  |
| --- | --- | --- | --- | --- |
|  | Circuit Integrity |  | CEI 20-36/2-1; SS229-1; NBN C 30-004 (cat. F3); |  |
|  |  |  | NF C32-070-2.3(CR1) |  |
|  | System circuit integrity |  | DIN 4102-12, E30 depending on lay system |  |
|  | Flame Retardance (Single Vertical |  | EN 60332-1-2; IEC 60332-1-2; BS EN 60332-1-2; VDE |  |
|  | Wire Test) |  | 0482-332-1 ; NBN C 30-004 (cat. F1); NF C32-070-2.1(C2); |  |
|  |  |  | CEI 20-35/1-2; EN 50265-2-1*; DIN VDE 0482-265-2-1* |  |
|  | Reduced Fire Propagation |  | EN 60332-3-24 (cat. C); IEC 60332-3-24; BS EN 60332-3-24; |  |
|  | (Vertically-mounted bundled wires |  | VDE 0482-332-3; NBN C 30-004 (cat. F2); NF C32-070-2.2(C1); |  |
|  | & cable test) |  | CEI 20-22/3-4; EN 50266-2-4*; DIN VDE 0482-266-2-4 |  |
|  | Halogen Free |  | IEC 60754-1; EN 50267-2-1; DIN VDE 0482-267-2-1; |  |
|  |  |  | CEI 20-37/2-1 ; BS 6425-1* |  |
|  | No Corrosive Gas Emission |  | IEC 60754-2; EN 50267-2-2; DIN VDE 0482-267-2-2; |  |
|  |  |  | CEI 20-37/2-2 ; BS 6425-2* |  |
|  | Minimum Smoke Emission |  | IEC 61034-1&2; EN 61034 -1&2; DIN VDE 0482-1034-1&2; |  |
|  |  |  | CEI 20-37/3-1&2; EN 50268-1&2*; BS 7622-1&2* |  |
| 112 | Caledonian | sales@caledonian-cables.net uk@caledonian-cables.net |  |  |

Caledonian

Fire Resistant Signal & Data Cables

www.caledonian-tech.net	www.caledonian-tech.com

| No Toxic gases | NES 02-713; NF C 20-454 |
| --- | --- |

Note: Asterisk * denotes superseded standard.

VOLTAGE RATING

60V

CABLE CONSTRUCTION

Conductors: Plain annealed copper wire, solid according to IEC(EN) 60228 class 1.

Insulation: PE wrapped with fire resistant silicone rubber compound type EI2 as per BS 7655-1.1.

Twisted Pairs: Insulated conductors are twisted into pairs with varying lay length to minimize crosstalk.

Cabling Elements: Insulated cores are twisted to form pairs with varying lay length to minimize crosstalk. Two-pair cable had four cores laid in quad formation.

Cabling: Pairs are cabled together in concentric layers.

Outer Sheath: Thermoplastic LSZH compound type LTS3 as per BS 7655-6.1 (Thermosetting LSZH compound type SW2-SW4 as per BS 7655-2.6 can be offered.)

Physical AND THERMAL PROPERTIES

Temperature range during operation (fixed state):-5°C - +50°C

Temperature range during installation (mobile state): -20°C - +90°C Minimum bending radius: 8 x Overall Diameter

Electrical Properties

| Characteristic Impedance | 100 Ohm±15% |
| --- | --- |
| Nominal Velocity of Propagation (NVP) | 69% |
| Max. Dc Resistance | 9.38 Ohm/100m |
| Max. Resistance Unbalance | 5% |
| Max. Mutual Capacitance: | 5.6 nF/100m |
| Maximum Capacitance Unbalance | 330 pF/100m |
| Max. Propagation Delay Skew | 30 ns/100m |
| Max. Propagation Delay | 536 ns/100m@100 mhz |
| Max. Pulling Load | 80N |

ADDISON   113

ADDISON

| Transmission Properties |  |  |  |  |
| --- | --- | --- | --- | --- |
| FREQ | NEXT(dB/100m) | IL | SRL (dB/100m) |  |
|  | Minimum Value/Typical Value/ |  | Minimum Value/Typical Value/ |  |
| (MHz) |  | (dB/100m) |  |  |
|  | Standard Value |  | Standard Value |  |
| 1 | 64.0/71.0/62.0 | 2.0 | 24.5/26.0/23.0 |  |
| 4 | 55.0/62.0/53.0 | 4.0 | 24.5/26.0/23.0 |  |
| 8 | 49.5/57.0/48.0 | 5.7 | 24.5/26.0/23.0 |  |
| 10 | 49.0/56.0/47.0 | 6.4 | 24.5/26.0/23.0 |  |
| 16 | 44.9/52.0/44.0 | 8.2 | 24.5/26.0/23.0 |  |
| 20 | 42.5/48.0/42.0 | 9.2 | 24.5/26.0/23.0 |  |
| 25 | 42.0/48.0/41.0 | 10.3 | 24.5/26.0/23.0 |  |
| 31.25 | 40.6/48.0/39.0 | 11.6 | 22.5/24.0/21.0 |  |
| 62.5 | 36.1/43.0/35.0 | 16.9 | 19.5/22.0/18.0 |  |
| 100 | 34.0/40.0/32.0 | 21.8 | 17.5/20.0/16.0 |  |

CONSTRUCTION PARAMETERS

|  | Conductor | Nominal | Nominal |  |
| --- | --- | --- | --- | --- |
| Cable Code |  | Insulation | Overall |  |
|  | Diameter |  |  |  |
|  |  | Thickness | Diameter |  |
|  | mm | mm | mm |  |
| FFX-CAT5UTP4P24FR | 0.5 | 0.25 | 5.3 |  |

60V	NEN50173

W

E

|  |  | Circuit Integrity | Reduced Fire Propagation | Flame Retardancy |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Rated Voltage | Standard | IEC 60331/BS 6387 | NF C32-070-2.2(C1) | NF C32-070-2.1(C2) |  |  |
|  |  | NF C32-070-2.3(CR1) | IEC60332-3-24/EN50266-2-4 IEC60332-1-2/EN50265-2-1 |  |  |  |
|  |  |  | Zero | W | E |  |
|  | Low Corrosivity | Low Smoke Emission | Halogen Free |  |  |  |
|  | IEC60754-2 |  |  |  |  |  |
| Low Toxicity |  | IEC 61034-1&2 | IEC60754-1 |  |  |  |
|  | EN50267-2-2/3 |  |  | Functional Integrity |  |  |
| NES 02-713/NF C 20-454 | NF C 32-074 | EN 50268-1&2/NF C32-073 | EN50267-2-1 |  | DIN 4102-12 |  |

114	Caledonian   sales@caledonian-cables.net   uk@caledonian-cables.net