ADDISON

Fire resistant RG6 QUAD Coaxial cables

RG6 QUAD FR

LSZH Outer Sheath

AL Foil+AL Braid

Glass Tape

Copper Clad Steel

(PE+Silicone Rubber)/FEP Insulation

AL Foil+AL Braid

APPLICATION

The cables are designed for CCTV, security, smoke detection and evacuation monitoring applications, where continued functionality is required during a fire situationDue. to the zero halogen low smoke construction, this cable is ideal for use in public, commercial and industrial environments.

Standards

Basic design to MIL-C-17

FIRE PERFORMANCE

|  | IEC 60331-23; BS 6387 CWZ; DIN VDE 0472-814(FE180); |  |
| --- | --- | --- |
| Circuit Integrity | CEI 20-36/2-1; SS229-1; NBN C 30-004 (cat. F3); |  |
|  | NF C32-070-2.3(CR1) |  |
| System circuit integrity | DIN 4102-12, E30 depending on lay system |  |
| Flame Retardance (Single Vertical | EN 60332-1-2; IEC 60332-1-2; BS EN 60332-1-2; VDE |  |
| Wire Test) | 0482-332-1 ; NBN C 30-004 (cat. F1); NF C32-070-2.1(C2); |  |
|  | CEI 20-35/1-2; EN 50265-2-1*; DIN VDE 0482-265-2-1* |  |
| Reduced Fire Propagation | EN 60332-3-24 (cat. C); IEC 60332-3-24; BS EN 60332-3-24; |  |
| (Vertically-mounted bundled wires | VDE 0482-332-3; NBN C 30-004 (cat. F2); NF C32-070-2.2(C1); |  |
| & cable test) | CEI 20-22/3-4; EN 50266-2-4*; DIN VDE 0482-266-2-4 |  |
| Halogen Free | IEC 60754-1; EN 50267-2-1; DIN VDE 0482-267-2-1; |  |
|  | CEI 20-37/2-1 ; BS 6425-1* |  |
| No Corrosive Gas Emission | IEC 60754-2; EN 50267-2-2; DIN VDE 0482-267-2-2; |  |
|  | CEI 20-37/2-2 ; BS 6425-2* |  |
| Minimum Smoke Emission | IEC 61034-1&2; EN 61034 -1&2; DIN VDE 0482-1034-1&2; |  |
|  | CEI 20-37/3-1&2; EN 50268-1&2*; BS 7622-1&2* |  |
| No Toxic gases | NES 02-713; NF C 20-454 |  |

Note: Asterisk * denotes superseded standard.

126	Caledonian   sales@caledonian-cables.net   uk@caledonian-cables.net

Caledonian

Fire Resistant Coaxial Cables

www.caledonian-tech.net	www.caledonian-tech.com

CABLE CONSTRUCTION

Conductors: Copper clad steel, solid according to IEC(EN) 60228 class 1.

Insulation: Foamed PE wrapped with fire resistant silicone rubber compound type EI2 as per BS 7655-1.1 or fluoropolymer(FEP) compound.

Binder: Glass tape

Overall Screen:

Screen1: Al-maylar Tape ≥25% Screen2: Aluminium Braid Screen3: Al-maylar Tape ≥25% Screen4: Aluminium Braid

Outer Sheath: Thermoplastic LSZH compound type LTS3 as per BS 7655-6.1 (Thermosetting LSZH compound type SW2-SW4 as per BS 7655-2.6 can be offered.)

Physical AND THERMAL PROPERTIES

Temperature range during operation (fixed state):-30°C - +70°C

Temperature range during installation (mobile state): -5ºC - +60ºC

Minimum bending radius: 8 x Overall Diameter

Electrical Properties

| Impedance | 75±5Ω |
| --- | --- |
| Capacitance | 54 nF/km |
| Velocity ratio(%) | 82 |
| Insulation resistance | >5000 Mohm.Km |
| Shield coverage | ≥60% |
| Max.conductor resistance | 24.1 Ω/km |

Attenuation

| Frequency(MHz) | Attenuation (dB/100 m) | Attenuation (dB/100ft) |
| --- | --- | --- |
| 50 | 4.8 | 1.5 |
| 100 | 6.7 | 2.0 |
| 200 | 9.3 | 2.8 |
| 500 | 15.0 | 4.6 |
| 600 | 16.9 | 5.1 |
| 800 | 19.4 | 5.9 |
| 1000 | 21.6 | 6.6 |
| 1350 | 24.2 | 7.4 |
| 1750 | 28.0 | 8.4 |
| 2150 | 31.5 | 9.6 |

ADDISON   127

ADDISON

| 2400 | 32.8 | 10.0 |  |
| --- | --- | --- | --- |
| 3000 | 37.9 | 11.5 |  |

Return Loss

| Frequency(MHz) | Return Loss (dB) |
| --- | --- |
| 30-300 | >28dB |
| 300-600 | >24dB |
| 600-900 | >22dB |

CONSTRUCTION PARAMETERS

| Cable | Conductor | Nominal | Nominal | Nominal | Nominal | Approx. |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Insulation | Screen2 | Screen4 | Overall |  |  |
| Code | Diameter |  |  |  |  | Weight |  |
|  |  | Diameter | No.x Diameter | No.x Diameter | Diameter |  |  |
|  | mm | mm | No. x mm | No. x mm | mm | kg/km |  |
| RG6 QUAD FR | 1.02 | 4.60 ± 0.20 | 80 x 0.12 | 64 x 0.12 | 7.55 ± 0.20 | 92.4 |  |

300/500V	NMIL-C-17

W

E

|  |  | Circuit Integrity | Reduced Fire Propagation | Flame Retardancy |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | IEC 60331/BS 6387 | NF C32-070-2.2(C1) | NF C32-070-2.1(C2) |  |  |
| Rated Voltage | Standard | NF C32-070-2.3(CR1) | IEC60332-3-24/EN50266-2-4 IEC60332-1-2/EN50265-2-1 |  |  |  |
|  |  |  | Zero | W | E |  |
|  | Low Corrosivity | Low Smoke Emission | Halogen Free |  |  |  |
| Low Toxicity | IEC60754-2 | IEC 61034-1&2 | IEC60754-1 | Functional Integrity |  |  |
|  | EN50267-2-2/3 |  |  |  |  |  |
| NES 02-713/NF C 20-454 |  | EN 50268-1&2/NF C32-073 | EN50267-2-1 |  |  |  |
|  | NF C 32-074 |  |  |  | DIN 4102-12 |  |

128	Caledonian   sales@caledonian-cables.net   uk@caledonian-cables.net