Date: 13 May 2011

Part No.: PS80705

Fire Resistant Speaker Cables

Application                                        Preferably used for installation into conduit and surface wiring which provide flame retardant, low smoke & corrosive gases properties and maintain circuit integrity in case of fire.

Construction

LSZH Outer Jacket

Overall Aluminum Screen

XLPE Insulation

Mica Tape Fire Barrier

Tinned Copper Wire Conductor

Tinned Copper Drain Wire

Conductor: Class 2 stranded tinned copper wire

Insulation: Cross-linked polyethylene (XLPE)

Twisting: Two insulated conductors uniformly twisted together to form a pair.

Pair Identification: 1) Black/Blue; 2) Black/Green;

3) Blue/Green; 4) Black/Brown;

5) Blue/Brown; 6) Green/Brown

7) Black/White; 8) Blue/White

9) Green/White; 10) Brown/White

Overall Collective Screen: Aluminum/polyester tape applied with the metallic side down in electrical contact with a 0.5mm² tinned copper drain wire. A 23 micron isolation tape is applied over the screening tape with a minimum 50% overlap.

Jacket: Low smoke & halogen free compound (LSZH)

Jacket Color: Black

Packing: Delivered on non-returnable wooden drums.

Physical Characteristics

Voltage Rating: 300/500V

Temperature Rating: During Operation: -40°C to +90°C

During Installation: 0°C to +50°C

Minimum Bending Radius: 6 x overall diameter

Fire Performance

Flame Retardant: IEC 60332 part 1 and part 3

Fire Resistant: IEC60331, BS6387 CWZ

Low Smoke Emission: IEC 61034

Zero Halogen Gas Emission: IEC 60754

Oxygen Index: ≥35%

Technical Data

| No. of Pair | Size of Conductor | Conductor Stranding | Insulation Thickness | Sheath Thickness | Overall Diameter |
| --- | --- | --- | --- | --- | --- |
| No. | mm2 | No./mm | mm | mm | mm |
| 2 | 1.00 | 32/0.20 | 0.60 | 0.80 | 11.00 |
| 2 | 2.50 | 50/0.25 | 0.80 | 1.10 | 17.00 |
| 2 | 4.00 | 56/0.30 | 0.80 | 1.20 | 19.00 |
| 10 | 2.50 | 50/0.25 | 0.80 | 1.50 | 34.00 |
| 10 | 4.00 | 56/0.30 | 0.80 | 1.80 | 39.50 |

The data included in the present catalogue are merely indicative; Caledonian Cables Limited reserves to itself the right to change them as its own discretion in any time.