Date: 05 Aug. 2011

File No.: PI80551

Fire Resistance Instrument Cable to IEC60331

300/500V 1X2X1.5mmsq Stranded Tinned Cu/SIR( Mica+XLPE)/OSCR/FRLSHF/SWB/FR-PVC

Application

Instrumentation cables are designed for transmission of analog and digital signals, and the interconnection of electrical equipment, such as monitoring or controlling electrical power systems and instruments, particular for the process control industry. The armoured versions are suitable for direct burial or installed in the duct.

On request, the outer sheath is oil, solvent, and hydrocarbon resistant, suitable for chemical and petrochemical environments.

Standard

- BS5308

- Fire Resistance: IEC 60331-21

- Flame Retardancy: IEC 60332-1

- Corrosive Acid Gas Emission: IEC 60754-1,2

- Smoke Emissions: IEC 61034-1,2

Construction

Tinned Copper Conductor

SIR /Mica+XLPE Insulation

A/P Screen

FRLSHF Inner Sheath

Steel Wire Braiding

FR-PVC Outer Jacket

Conductors:   	Stranded Tinned copper wire to IEC 60228 class 2.

1.5mmsq=7/0.53mm

Insulation:     	SIR (or Mica glass tape + XLPE)

Core Color:    	Black/White

Twisting:      	The cores shall twist together in pair

Overall Screen: 	Aluminium/ p.e.t.p. laminated tape applied with the metallic side in contact with a 0.5mm2 tinned copper drain wire over the p.e.t.p. binder tape.

A 23 micron polyester tape is applied over the screening tape with a minimum 25% overlap.

Bedding:       	FRLSHF PO compound

Armour:        	One layer of galvanized steel wire braiding, coverage≥95%

Outer Sheath:   	FR-PVC compound, which is Hydrocarbon, UV & Oil Resisting

Sheath Color:   	Black with red strip

Packing:            	The cables are delivered on non-returnable drums.

Technical data

| Size of Conductor | Nominal Insulation Thickness (mm) | Nominal Sheath Thickness (mm) |  | Nominal Overall Diameter (mm) | Nominal Weight (kg/km) |
| --- | --- | --- | --- | --- | --- |
|  |  | Inner | Outer |  |  |
| 1×2×1.5mmsq | 0.7 | 0.8 | 1.4 | 11.6 | 195 |

Physical characteristics

Temperature rating:

- During operation: -20 to + 70℃

- During Installation: 0 to + 70℃

Minimum bending radius:

During installation: 5 x Overall Diameter

Fire resistance:         IEC60331

Flame retardant:        IEC60332-1

Flexibility:              Rigid

Electrical characteristics

Rated voltage:                         	300/500V

Max. conductor resistance at 20ºC:      	<12.3 ohm/km

Min insulation resistance:             		≥5G Ohm×Km

Max inductance / resistance (L/R) ratio: 		<60 uH/ Ohm

Max. mutual capacitance at 1KHz:       	115 pF/m

Test voltage:

- core:core                         	2000V

- core:screen                        	1000V